## OTC State Regs
State | Type of Emissions Unit | Pollutant | Unit Size |  | Fuel | Emission Limit |  | Regulatory Citation | Notes 1 | Notes 2 | Notes 3 | Notes 4 | Notes 5 | Notes 6
CT | Fuel Burning Equipment | PM | All |  | NG | 0.1 | lb/MMBtu | 22a-174-18(e)(2)
| Fuel Burning Equipment | PM | All |  | DO | 0.12 | lb/MMBtu | 22a-174-18(e)(2)
| Fuel Burning Equipment | PM | All |  | RO | 0.14 | lb/MMBtu | 22a-174-18(e)(2)
| Fuel Burning Equipment | PM | All |  | Other | 0.2 | lb/MMBtu | 22a-174-18(e)(2)
| Fuel Burning Equipment, Eff 1/1/02 | SO2 | All |  | NG/DO/RO | 0.55 | lb/MMBtu | 22a-174-19a(c)(2) | Effective 1/1/02 | Alternate: 0.5 lb/MMBtu avg for multiple units | Alternate: sulfur content < 0.5 wt%
| Fuel Burning Equipment, Eff 1/1/03 | SO2 | All |  | NG/DO/RO | 0.33 | lb/MMBtu | 22a-174-19a(e)(2) | Effective 1/1/03 | Alternate: 0.3 lb/MMBtu avg for multiple units | Alternate: sulfur content < 0.5 wt%
| Fuel Burning Equipment | SO2 | All |  | Other | 1.1 | lb/MMBtu | 22a-174-19(a)(3)(ii) |  |  | Alternate: sulfur content < 1.0 wt%
| Boiler - Cyclone | NOx | All |  | NG/DO/RO/Coal | 0.43 | lb/MMBtu | 22a-174-22(e)(1)
| Boiler - Fluidized Bed | NOx | All |  | Coal | 0.29 | lb/MMBtu | 22a-174-22(e)(1)
| Boiler - Other | NOx | All |  | NG/DO | 0.2 | lb/MMBtu | 22a-174-22(e)(1)
| Boiler - Other | NOx | All |  | RO | 0.25 | lb/MMBtu | 22a-174-22(e)(1)
| Boiler - Other | NOx | All |  | Coal | 0.38 | lb/MMBtu | 22a-174-22(e)(1)
| Turbine | NOx | ≥ 100 | MMBtu/hr | NG | 55 | ppmvd | 22a-174-22(e)(1) |  |  | Corrected to 15% O2
| Turbine | NOx | ≥ 100 | MMBtu/hr | DO | 75 | ppmvd | 22a-174-22(e)(1) |  |  | Corrected to 15% O2
| Turbine | NOx | < 100 | MMBtu/hr | NG/DO | 0.9 | lb/MMBtu | 22a-174-22(e)(1)
| Fuel Burning Equipment | NOx | All |  | Other | 0.3 | lb/MMBtu | 22a-174-22(e)(2)
DE | Fuel Burning Equipment | PM | All |  | Any | 0.3 | lb/MMBtu | Reg. 4, Section 2.1
| Fuel Burning Equipment | SO2 | All |  | DO | 0.3 | wt% sulfur | Reg. 8, Section 2.2 | Statewide
| Fuel Burning Equipment | SO2 | All |  | Any | 1 | wt% sulfur | Reg. 8, Section 2.1 | New Castle County only
| Boiler - Face/Tangential | NOx | All |  | NG | 0.2 | lb/MMBtu | Reg. 12, Section 3.2.a
| Boiler - Face/Tangential | NOx | All |  | Oil or Oil/NG | 0.25 | lb/MMBtu | Reg. 12, Section 3.2.a
| Boiler - Face/Tangential | NOx | All |  | Coal | 0.38 | lb/MMBtu | Reg. 12, Section 3.2.a
| Boiler - Cyclone | NOx | All |  | Oil | 0.43 | lb/MMBtu | Reg. 12, Section 3.2.a
| Boiler - Stoker | NOx | All |  | Coal | 0.4 | lb/MMBtu | Reg. 12, Section 3.2.a
DC | Fuel Burning Equipment | PM | < 3.5 |  | Any | 0.13 | lb/MMBtu | Title 20, Section 600.1
| Fuel Burning Equipment | PM | 3.5 - 9,999 |  | Any | Formula | lb/MMBtu | Title 20, Section 600.1 | Based on a formula: E (lb/MMBtu) = 0.17455 H-0.23522, where H = MMBtu/hr input rating of the unit
| Fuel Burning Equipment | PM | ≥ 10,000 |  | Any | 0.02 | lb/MMBtu | Title 20, Section 600.1
| Fuel Burning Equipment | SO2 | All |  | Any | 0.05 | vol % | Title 20, Section 803.1 | 0.05 vol% = 500 ppmv | Dry or wet not specified, O2 correction not specified
| Fuel Burning Equipment | SO2 | All |  | Oil/Coal | 1 | wt% sulfur | Title 20, Section 801.1 / 802.1
| Boiler | NOx | > 100 | MMBtu/hr | NG | 0.2 | lb/MMBtu | Title 20, Section 804.1
| Boiler | NOx | > 100 | MMBtu/hr | Oil | 0.3 | lb/MMBtu | Title 20, Section 804.1
| Boiler | NOx | > 100 | MMBtu/hr | Solid | 0.7 | lb/MMBtu | Title 20, Section 804.1 | Solid fuel includes coal, except lignite
| Boiler - Face/Tangential | NOx | 50 - 99 | MMBtu/hr | Oil | 0.3 | lb/MMBtu | Title 20, Section 805.5(b) | RACT - Major sources only
| Boiler - Face/Tangential | NOx | ≥ 100 | MMBtu/hr | NG | 0.2 | lb/MMBtu | Title 20, Section 805.5(c)(2) | RACT - Major sources only
| Boiler - Face/Tangential | NOx | ≥ 100 | MMBtu/hr | Oil | 0.25 | lb/MMBtu | Title 20, Section 805.5(c)(2) | RACT - Major sources only
| Boiler - Face/Tangential/Stoker | NOx | ≥ 100 | MMBtu/hr | Coal | 0.43 | lb/MMBtu | Title 20, Section 805.5(c)(1) | RACT - Major sources only
| Turbine | NOx | ≥ 100 | MMBtu/hr | Oil | 75 | ppmvd | Title 20, Section 805.4(a)(1) | RACT - Major sources only |  | Corrected to 15% O2
ME | Fuel Burning Equipment, Pre-12/2/82 | PM | All |  | NG/DO/RO | 0.2 | lb/MMBtu | 6-96-103.2(A)(1)
| Fuel Burning Equipment, Pre-12/2/82 | PM | < 50 | MMBtu/hr | Coal | 0.3 | lb/MMBtu | 6-96-103.2(A)(2)(a)
| Fuel Burning Equipment, Pre-12/2/82 | PM | ≥ 50 | MMBtu/hr | Coal | 0.08 | lb/MMBtu | 6-96-103.2(A)(2)(b)
| Fuel Burning Equipment, Pre-12/2/82 | PM | < 150 | MMBtu/hr | Wood | Formula | lb/MMBtu | 6-96-103.2(A)(3)(a) | Based on a formula: log(y) = 0.034 - 0.256 log(x), where y = lb/MMBtu emission factor, x = MMBtu input rating of the unit
| Fuel Burning Equipment, Pre-12/2/82 | PM | ≥ 150 | MMBtu/hr | Wood | 0.3 | lb/MMBtu | 6-96-103.2(A)(3)(b)
| Fuel Burning Equipment, Post-12/2/82 | PM | < 50 | MMBtu/hr | NG/DO/RO | 0.12 | lb/MMBtu | 6-96-103.2(B)(1)(a)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 50 | MMBtu/hr | NG/DO/RO | 0.08 | lb/MMBtu | 6-96-103.2(B)(1)(b)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 250 | MMBtu/hr | NG/DO/RO | 0.06 | lb/MMBtu | 6-96-103.2(B)(1)(c)
| Fuel Burning Equipment, Post-12/2/82 | PM | < 50 | MMBtu/hr | Solid Waste | 0.3 | lb/MMBtu | 6-96-103.2(B)(2)(a)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 50 | MMBtu/hr | Solid Waste | 0.2 | lb/MMBtu | 6-96-103.2(B)(2)(b)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 250 | MMBtu/hr | Solid Waste | 0.1 | lb/MMBtu | 6-96-103.2(B)(2)(c)
| Fuel Burning Equipment, Post-12/2/82 | PM | < 50 | MMBtu/hr | Coal | 0.3 | lb/MMBtu | 6-96-103.2(B)(3)(a)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 50 | MMBtu/hr | Coal | 0.08 | lb/MMBtu | 6-96-103.2(B)(3)(b)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 250 | MMBtu/hr | Coal | 0.05 | lb/MMBtu | 6-96-103.2(B)(3)(c)
| Fuel Burning Equipment, Post-12/2/82 | PM | < 50 | MMBtu/hr | Wood/Coal/Biomass | 0.3 | lb/MMBtu | 6-96-103.2(B)(4)(a)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 50 | MMBtu/hr | Wood/Coal/Biomass | 0.08 | lb/MMBtu | 6-96-103.2(B)(4)(b)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 250 | MMBtu/hr | Wood/Coal/Biomass | 0.06 | lb/MMBtu | 6-96-103.2(B)(4)(c)
| Fuel Burning Equipment, Post-12/2/82 | PM | ≥ 50 | MMBtu/hr | Wood/Coal/Biomass | 0.1 | lb/MMBtu | 6-96-103.2(B)(4)(d) | Applies when using venturi scrubber, i.e., exempt from 6-96-103.2.B(4)(b) and (c)
| Fuel Burning Equipment | SO2 | All |  | DO/RO | 2 | wt% sulfur | 6-96-106.2(A)(2) | Statewide | Fuel blending allowed per 6-96-106.5
| Fuel Burning Equipment | SO2 | All |  | DO/RO | 1.5 | wt% sulfur | 6-96-106.2(A)(3) | Portland Peninsula AQR only | Fuel blending allowed per 6-96-106.5
| Fuel Burning Equipment | SO2 | All |  | Coal | 0.96 | lb S/MMBtu | 6-96-106.2(B)(2) | Statewide | Fuel blending allowed per 6-96-106.5
| Fuel Burning Equipment | SO2 | All |  | Coal | 0.72 | lb S/MMBtu | 6-96-106.2(B)(3) | Portland Peninsula AQR only | Fuel blending allowed per 6-96-106.5
| Fuel Burning Equipment | SO2 | All |  | Any | 1.92 | lb/MMBtu | 6-96-106.4(B) | Statewide | When using FGD or other sulfur removal device, i.e., exempt from 6-96-106.2 fuel sulfur content
| Fuel Burning Equipment | SO2 | All |  | Any | 1.57 | lb/MMBtu | 6-96-106.4(C) | Portland Peninsula AQR only | When using FGD or other sulfur removal device, i.e., exempt from 6-96-106.2 fuel sulfur content
| Boiler | NOx | ≥ 1,500 | MMBtu/hr | Any | 0.3 | lb/MMBtu | 6-96-138.3(A) | Statewide | RACT - Major sources only | Alternate: 0.2 (O3 season), 0.3 (rest) | Alternate: 0.15 (O3 season), 0.35 (rest) | Emissions averaging across units allowed | Alternate: Apply RACT (LNB, OFA, SCR/SNCR, fuel change, alt. oper. scenario, etc.)
| Boiler | NOx | 50 - 1,499 | MMBtu/hr | Oil/Biomass/NG | 0.3 | lb/MMBtu | 6-96-138.3(B) | Moderate non-attainment areas only | RACT - Major sources only | Alternate: 0.2 (O3 season), 0.4 (rest) | Alternate: 0.15 (O3 season), 0.45 (rest) | Emissions averaging across units allowed | Alternate: Apply RACT (LNB, OFA, SCR/SNCR, fuel change, alt. oper. scenario, etc.)
| Boiler | NOx | 50 - 1,499 | MMBtu/hr | Biomass & Coal | 0.38 | lb/MMBtu | 6-96-138.3(B) | Moderate non-attainment areas only | RACT - Major sources only | Alternate: 0.2 (O3 season), 0.4 (rest) | Alternate: 0.15 (O3 season), 0.45 (rest) | Emissions averaging across units allowed | Alternate: Apply RACT (LNB, OFA, SCR/SNCR, fuel change, alt. oper. scenario, etc.)
| Boiler | NOx | 50 - 1,499 | MMBtu/hr | Biomass/NG | 0.3 | lb/MMBtu | 6-96-138.4 | Attainment areas only | RACT - Major sources only |  |  | Emissions averaging across units allowed | Alternate: Apply RACT (LNB, OFA, SCR/SNCR, fuel change, alt. oper. scenario, etc.)
| Boiler | NOx | 50 - 1,499 | MMBtu/hr | Oil | 0.4 | lb/MMBtu | 6-96-138.4 | Attainment areas only | RACT - Major sources only |  |  | Emissions averaging across units allowed | Alternate: Apply RACT (LNB, OFA, SCR/SNCR, fuel change, alt. oper. scenario, etc.)
| Boiler | NOx | 50 - 1,499 | MMBtu/hr | Biomass & Coal | 0.45 | lb/MMBtu | 6-96-138.4 | Attainment areas only | RACT - Major sources only |  |  | Emissions averaging across units allowed | Alternate: Apply RACT (LNB, OFA, SCR/SNCR, fuel change, alt. oper. scenario, etc.)
| Boiler - Kraft Recovery | NOx | All |  | Any | 120 | ppmvw | 6-96-138.3(C) | Statewide | RACT - Major sources only | Corrected to 8% O2 or 12% CO2 |  | Emissions averaging across units allowed | Alternate: Apply RACT (LNB, OFA, SCR/SNCR, fuel change, alt. oper. scenario, etc.)
| EGU ≥ 25 MW | NOx | < 750 | MMBtu/hr | Fossil | 0.22 | lb/MMBtu | 6-96-145.3(B)(2)(a) | Counties not waived under section 182(f) of the 1990 CAAA (York, Cumberland, Sagadahoc, Androscoggin, Kennebec, Lincoln and Knox) |  |  |  | Emissions averaging across units allowed
| EGU ≥ 25 MW | NOx | ≥ 750 | MMBtu/hr | Fossil | 0.15 | lb/MMBtu | 6-96-145.3(B)(2)(b) | Counties not waived under section 182(f) of the 1990 CAAA (York, Cumberland, Sagadahoc, Androscoggin, Kennebec, Lincoln and Knox) |  |  |  | Emissions averaging across units allowed
| Boiler - non-EGU | NOx | ≥ 250 | MMBtu/hr | Fossil | 0.2 | lb/MMBtu | 6-96-145.3(B)(2)(c) | Counties not waived under section 182(f) of the 1990 CAAA (York, Cumberland, Sagadahoc, Androscoggin, Kennebec, Lincoln and Knox) |  |  |  |  | Includes indirect heat exchangers, primary boilers and resource recovery units
MD | Fuel Burning Equipment, Pre-01/17/72 | PM | < 10 | MMBtu/hr | RO/Solid | 0.6 | lb/MMBtu | 26.11.09.06(A)(1) | Areas I, II, V & VI only
| Fuel Burning Equipment, Pre-01/17/72 | PM | ≥ 10 | MMBtu/hr | RO/Solid | Formula | lb/MMBtu | 26.11.09.06(A)(1) | Areas I, II, V & VI only | Based on a formula: E (lb/MMBtu) = 1.025985 H-0.23299, where H = MMBtu input rating of the unit
| Fuel Burning Equipment, Post-01/17/72 | PM | < 25 | MMBtu/hr | RO/Solid | 0.4 | lb/MMBtu | 26.11.09.06(A)(2) | Areas I, II, V & VI only
| Fuel Burning Equipment, Post-01/17/72 | PM | 25 - 249 | MMBtu/hr | RO/Solid | Formula | lb/MMBtu | 26.11.09.06(A)(2) | Areas I, II, V & VI only | Based on a formula: E = log10[6.597538 (H)-0.3], where E = lb/MMBtu emission factor, H = MMBtu input rating of the unit
| Fuel Burning Equipment, Post-01/17/72 | PM | ≥ 250 | MMBtu/hr | RO/Solid | 0.1 | lb/MMBtu | 26.11.09.06(A)(2) | Areas I, II, V & VI only
| Fuel Burning Equipment | PM | 13 - 50 | MMBtu/hr | RO | 0.03 | gr/dscf | 26.11.09.06(B)(2) | Areas III & IV only (Baltimore & Washington metropolitan areas)
| Fuel Burning Equipment | PM | 50 - 250 | MMBtu/hr | RO | 0.02 | gr/dscf | 26.11.09.06(B)(2) | Areas III & IV only (Baltimore & Washington metropolitan areas)
| Fuel Burning Equipment, Pre-07/01/75 | PM | > 250 | MMBtu/hr | RO | 0.02 | gr/dscf | 26.11.09.06(B)(2) | Areas III & IV only (Baltimore & Washington metropolitan areas)
| Fuel Burning Equipment, Post-07/01/75 | PM | > 250 | MMBtu/hr | RO | 0.01 | gr/dscf | 26.11.09.06(B)(2) | Areas III & IV only (Baltimore & Washington metropolitan areas)
| Fuel Burning Equipment, Pre-07/01/75 | PM | < 250 | MMBtu/hr | Solid | 0.05 | gr/dscf | 26.11.09.06(B)(3) | Areas III & IV only (Baltimore & Washington metropolitan areas)
| Fuel Burning Equipment, Post-07/01/75 | PM | < 250 | MMBtu/hr | Solid | 0.03 | gr/dscf | 26.11.09.06(B)(3) | Areas III & IV only (Baltimore & Washington metropolitan areas)
| Fuel Burning Equipment | PM | ≥ 250 | MMBtu/hr | Solid | 0.03 | gr/dscf | 26.11.09.06(B)(3) | Areas III & IV only (Baltimore & Washington metropolitan areas)
| Fuel Burning Equipment | SO2 | All |  | Process Gas | 0.3 | wt% sulfur | 26.11.09.07(A)(1) | Areas I, II, V & VI only
| Fuel Burning Equipment | SO2 | All |  | DO | 0.3 | wt% sulfur | 26.11.09.07(A)(1) | Areas I, II, V & VI only
| Fuel Burning Equipment | SO2 | All |  | RO | 2 | wt% sulfur | 26.11.09.07(A)(1) | Areas I, II, V & VI only |  |  | Area I exception: 1.0 wt% sulfur limit, if NAAQS/PSD increment violation
| Fuel Burning Equipment | SO2 | All |  | Solid | 3.5 | lb/MMBtu | 26.11.09.07(A)(1) | Areas I, II, V & VI only | Only applies if all fuel burning equipment at the facility combined ≥ 100 MMBtu/hr |  | Area I exception: 1.8 lb SO2/MMBtu limit, if NAAQS/PSD increment violation
| Fuel Burning Equipment | SO2 | All |  | DO | 0.3 | wt% sulfur | 26.11.09.07(A)(2) | Areas III & IV only
| Fuel Burning Equipment | SO2 | All |  | RO | 1 | wt% sulfur | 26.11.09.07(A)(2) | Areas III & IV only
| Fuel Burning Equipment | SO2 | All |  | Solid | 1 | wt% sulfur | 26.11.09.07(A)(2) | Areas III & IV only
| Fuel Burning Equipment | SO2 | > 1,000 | MMBtu/hr | Solid | 3.5 | lb/MMBtu | 26.11.09.07(B)(4) | Areas III & IV only | Only applies to existing units. It is unclear what "existing" means - no date specified.
| Fuel Burning Equipment | NOx | All |  | NG | 0.2 | lb/MMBtu | 26.11.09.08(B)(1)(c) | Major sources only | Emissions averaging across units and across facilities allowed
| Fuel Burning Equipment | NOx | All |  | Oil/NG | 0.25 | lb/MMBtu | 26.11.09.08(B)(1)(c) | Major sources only | Emissions averaging across units and across facilities allowed
| Fuel Burning Equipment - dry bottom | NOx | All |  | Coal | 0.38 | lb/MMBtu | 26.11.09.08(B)(1)(c) | Major sources only | Emissions averaging across units and across facilities allowed
| Fuel Burning Equipment - wet bottom | NOx | All |  | Coal | 1 | lb/MMBtu | 26.11.09.08(B)(1)(c) | Major sources only | Emissions averaging across units and across facilities allowed
| EGU | NOx | ≥ 250 | MMBtu/hr | Oil or Oil/NG | 0.3 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| EGU - Tangential | NOx | ≥ 250 | MMBtu/hr | Coal | 0.45 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| EGU - Wall | NOx | ≥ 250 | MMBtu/hr | Coal | 0.5 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| EGU - Tangential (High Heat Release) | NOx | ≥ 250 | MMBtu/hr | Coal | 0.7 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| EGU - Wall (High Heat Release) | NOx | ≥ 250 | MMBtu/hr | Coal | 0.8 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| EGU - Cell Burners | NOx | ≥ 250 | MMBtu/hr | Coal | 0.6 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| EGU - Cyclone (Ozone Season) | NOx | ≥ 250 | MMBtu/hr | Coal | 0.7 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| EGU - Cyclone (non-Ozone Season) | NOx | ≥ 250 | MMBtu/hr | Coal | 1.5 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| Non-EGU (Ozone Season) | NOx | ≥ 250 | MMBtu/hr | Any | 0.7 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| Non-EGU (non-Ozone Season) | NOx | ≥ 250 | MMBtu/hr | Any | 0.99 | lb/MMBtu | 26.11.09.08(C)(2) | Major sources only
| Fuel Burning Equipment | NOx | 100 - 249 | MMBtu/hr | Any | 0.65 | lb/MMBtu | 26.11.09.08(D)(1)(a) | Major sources only | Only applies to units > 15% capacity factor | Space heaters exempted
| Turbine | NOx | All | MMBtu/hr | NG | 42 | ppmvd | 26.11.09.08(G)(2) | Major sources only | Only applies to units > 15% capacity factor | Corrected to 15% O2
| Turbine | NOx | All | MMBtu/hr | Oil | 65 | ppmvd | 26.11.09.08(G)(2) | Major sources only | Only applies to units > 15% capacity factor | Corrected to 15% O2
MA | Fuel Burning Equipment - Pre-06/01/72 | PM | ≥ 3 | MMBtu/hr | Any | 0.12 | lb/MMBtu | 310 CMR 7.02(8)(d) | Communities listed in Table 3 of this regulation (except Worcester)
| Fuel Burning Equipment - Pre-06/01/72 | PM | ≥ 3 | MMBtu/hr | NG or DO | 0.1 | lb/MMBtu | 310 CMR 7.02(8)(d) | City of Worcester only
| Fuel Burning Equipment - Pre-06/01/72 | PM | ≥ 3 | MMBtu/hr | RO or Coal | 0.12 | lb/MMBtu | 310 CMR 7.02(8)(d) | City of Worcester only
| Fuel Burning Equipment - Pre-06/01/72 | PM | ≥ 3 | MMBtu/hr | Any | 0.15 | lb/MMBtu | 310 CMR 7.02(8)(e) | Rest of the State
| Fuel Burning Equipment - Post-06/01/72 | PM | ≥ 3 | MMBtu/hr | Wood | 0.1 | lb/MMBtu | 310 CMR 7.02(8)(h) | Communities listed in Table 3 of this regulation (including Worcester)
| Fuel Burning Equipment - Post-06/01/72 | PM | 3 - 25 | MMBtu/hr | Wood | 0.2 | lb/MMBtu | 310 CMR 7.02(8)(h) | Rest of the State
| Fuel Burning Equipment - Post-06/01/72 | PM | ≥ 25 | MMBtu/hr | Wood | 0.1 | lb/MMBtu | 310 CMR 7.02(8)(h) | Rest of the State
| Fuel Burning Equipment - Post-06/01/72 | PM | 3 - 250 | MMBtu/hr | Fossil | 0.1 | lb/MMBtu | 310 CMR 7.02(8)(h) | Statewide
| Fuel Burning Equipment - Post-06/01/72 | PM | ≥ 250 | MMBtu/hr | Fossil | 0.05 | lb/MMBtu | 310 CMR 7.02(8)(h) | Statewide
| Fuel Burning Equipment | SO2 | All |  | Fossil | 0.28 - 1.21 | lb S/MMBtu | 310 CMR 7.05(1)(a)(1) | Districts listed in Table 1 of this regulation (varies by district and portions of district)
| Fuel Burning Equipment | SO2 | All |  | DO | 0.17 | lb S/MMBtu | 310 CMR 7.05(1)(a)(2) | Statewide
| Fuel Burning Equipment | SO2 | ≥ 100 | MMBtu/hr | Oil or Coal | 1.21 | lb S/MMBtu | 310 CMR 7.05(1)(b)(1) | Districts listed in Table 1 of this regulation
| EGU | SO2 | ≥ 2,500 | MMBtu/hr | Oil or Coal | 0.55 | lb S/MMBtu | 310 CMR 7.05(1)(b)(2) | Certain towns within Metro Boston APCD listed in Table 1 of this regulation
| Entire State (All Sources of SO2) | SO2 | All |  | Any | 417000 | tons/yr | 310 CMR 7.21(2) | Statewide Emissions Cap
| Fuel Burning Equipment | SO2 | ≥ 100 | MMBtu/hr | Any | 1.2 | lb/MMBtu | 310 CMR 7.22(1) | Annual average, eff. 12/31/94 | Emissions averaging across units and across facilities within the State allowed |  | Emissions trading allowed within the State
| Entire Power Plant | SO2 | All |  | Any | 6 | lb/MWH | 310 CMR 7.29(5)(a)(2)(a) | Annual average, eff. 10/01/04 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Entire Power Plant, with any repowered unit | SO2 | All |  | Any | 6 | lb/MWH | 310 CMR 7.29(5)(a)(2)(a) | Annual average, eff. 10/01/06 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Entire Power Plant | SO2 | All |  | Any | 3 | lb/MWH | 310 CMR 7.29(5)(a)(2)(b) | Annual average, eff. 10/01/06 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Entire Power Plant, with any repowered unit | SO2 | All |  | Any | 3 | lb/MWH | 310 CMR 7.29(5)(a)(2)(b) | Annual average, eff. 10/01/08 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Entire Power Plant | SO2 | All |  | Any | 6 | lb/MWH | 310 CMR 7.29(5)(a)(2)(b) | Monthly average, eff. 10/01/06 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Entire Power Plant, with any repowered unit | SO2 | All |  | Any | 6 | lb/MWH | 310 CMR 7.29(5)(a)(2)(b) | Monthly average, eff. 10/01/08 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Boiler | NOx | All | MMBtu/hr | NG | 0.2 | lb/MMBtu | 310 CMR 7.19(4)(a)(5) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler (Heat Release ≤ 70,000 Btu/hours-ft3) | NOx | 100 - 249 | MMBtu/hr | Oil or Oil/NG | 0.3 | lb/MMBtu | 310 CMR 7.19(4)(a)(4) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler (Heat Release > 70,000 Btu/hours-ft3) | NOx | 100 - 249 | MMBtu/hr | Oil or Oil/NG | 0.4 | lb/MMBtu | 310 CMR 7.19(4)(a)(4) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Tangential | NOx | ≥ 250 | MMBtu/hr | NG | 0.2 | lb/MMBtu | 310 CMR 7.19(4)(a)(3) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Tangential | NOx | ≥ 250 | MMBtu/hr | Oil or Oil/NG | 0.25 | lb/MMBtu | 310 CMR 7.19(4)(a)(3) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiiler - Face Fired | NOx | ≥ 250 | MMBtu/hr | Oil/NG | 0.28 | lb/MMBtu | 310 CMR 7.19(4)(a)(3) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Stoker | NOx | ≥ 100 | MMBtu/hr | Solid (Not Coal) | 0.33 | lb/MMBtu | 310 CMR 7.19(4)(a)(2) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Dry Bottom, Tangential | NOx | ≥ 100 | MMBtu/hr | Coal | 0.38 | lb/MMBtu | 310 CMR 7.19(4)(a)(1) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Dry Bottom, Face Fired | NOx | ≥ 100 | MMBtu/hr | Coal | 0.45 | lb/MMBtu | 310 CMR 7.19(4)(a)(1) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Repowered | NOx | All | MMBtu/hr | Oil/NG | 0.1 | lb/MMBtu | 310 CMR 7.19(4)(b)(3) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Dry Bottom, Face/Tangential, Repowered | NOx | All | MMBtu/hr | Solid | 0.2 | lb/MMBtu | 310 CMR 7.19(4)(b)(3) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Face/Tangential | NOx | 50 - 99 | MMBtu/hr | NG | 0.1 | lb/MMBtu | 310 CMR 7.19(5)(a)(2) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Face/Tangential | NOx | 50 - 99 | MMBtu/hr | DO or DO/NG | 0.12 | lb/MMBtu | 310 CMR 7.19(5)(a)(2) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Face/Tangential | NOx | 50 - 99 | MMBtu/hr | RO or RO/NG | 0.3 | lb/MMBtu | 310 CMR 7.19(5)(a)(2) | RACT - Major sources only | Emissions averaging across units allowed | Required: 15% FGR, O2=3% at boiler exit | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Boiler - Face/Tangential/Stoker | NOx | 50 - 99 | MMBtu/hr | Solid | 0.43 | lb/MMBtu | 310 CMR 7.19(5)(a)(1) | RACT - Major sources only | Emissions averaging across units allowed |  | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Turbine - Combined Cycle | NOx | ≥ 25 | MMBtu/hr | NG | 42 | ppmvd | 310 CMR 7.19(7)(a)(1) | RACT - Major sources only | Emissions averaging across units allowed | Corrected to 15% O2 | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Turbine - Combined Cycle | NOx | ≥ 25 | MMBtu/hr | Oil | 65 | ppmvd | 310 CMR 7.19(7)(a)(1) | RACT - Major sources only | Emissions averaging across units allowed | Corrected to 15% O2 | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Turbine - Combined Cycle | NOx | ≥ 25 | MMBtu/hr | Oil/NG | 50 | ppmvd | 310 CMR 7.19(7)(a)(1) | RACT - Major sources only | Emissions averaging across units allowed | Corrected to 15% O2 | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Turbine - Simple Cycle | NOx | ≥ 25 | MMBtu/hr | NG | 65 | ppmvd | 310 CMR 7.19(7)(a)(2) | RACT - Major sources only | Emissions averaging across units allowed | Corrected to 15% O2 | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Turbine - Simple Cycle | NOx | ≥ 25 | MMBtu/hr | Oil | 100 | ppmvd | 310 CMR 7.19(7)(a)(2) | RACT - Major sources only | Emissions averaging across units allowed | Corrected to 15% O2 | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Turbine - Simple Cycle | NOx | ≥ 25 | MMBtu/hr | Oil/NG | 100 | ppmvd | 310 CMR 7.19(7)(a)(2) | RACT - Major sources only | Emissions averaging across units allowed | Corrected to 15% O2 | Alternate: If cannot meet limit, then Apply RACT (LNB, SOFA, SCR/SNCR/NSCR, fuel change, burner out of service, water/steam injection, etc.)
| Turbine - Post-03/23/06 | NOx | < 1 | MW | NG | 0.47 | lb/MWH | 310 CMR 7.26(43)(b)
| Turbine - Post-03/23/06 | NOx | 1 - 10 | MW | NG | 0.14 | lb/MWH | 310 CMR 7.26(43)(b)
| Turbine - Post-03/23/06 | NOx | 1 - 10 | MW | Oil | 0.34 | lb/MWH | 310 CMR 7.26(43)(b)
| Entire Power Plant | NOx | All |  | Any | 1.5 | lb/MWH | 310 CMR 7.29(5)(a)(1)(a) | Annual average, eff. 10/01/04 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Entire Power Plant, with any repowered unit | NOx | All |  | Any | 1.5 | lb/MWH | 310 CMR 7.29(5)(a)(1)(a) | Annual average, eff. 10/01/06 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Entire Power Plant | NOx | All |  | Any | 3 | lb/MWH | 310 CMR 7.29(5)(a)(1)(b) | Monthly average, eff. 10/01/06 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
| Entire Power Plant, with any repowered unit | NOx | All |  | Any | 3 | lb/MWH | 310 CMR 7.29(5)(a)(1)(b) | Monthly average, eff. 10/01/08 | Applies only to plants with SO2>500tpy (during 1997, 98 or 99) AND NOx>500tpy (during 1997, 98 or 99) AND have a boiler that (a) is subject to 40CFR72 (acid rain), (b) is >100MW, (c) is pre-08/07/77, (d) did not get a PSD permit prior to 10/31/98.
NH | Fuel Burning Equipment - Pre-05/13/70 | PM | < 10 | MMBtu/hr | Any | 0.6 | lb/MMBtu | Env-A 2002.06(c)(1)
| Fuel Burning Equipment - Pre-05/13/70 | PM | 10 - 9,999 | MMBtu/hr | Any | Formula | lb/MMBtu | Env-A 2002.06(c)(2) | Based on a formula: E (lb/MMBtu) = 0.880 H-0.166, where H = MMBtu/hr input rating of the unit
| Fuel Burning Equipment - Pre-05/13/70 | PM | ≥ 10,000 | MMBtu/hr | Any | 0.19 | lb/MMBtu | Env-A 2002.06(c)(3)
| Fuel Burning Equipment - 05/14/70 - 12/31/84 | PM | < 10 | MMBtu/hr | Any | 0.6 | lb/MMBtu | Env-A 2002.07(c)(1)
| Fuel Burning Equipment - 05/14/70 - 12/31/84 | PM | 10 - 249 | MMBtu/hr | Any | Formula | lb/MMBtu | Env-A 2002.07(c)(2) | Based on a formula: E (lb/MMBtu) = 1.028 H-0.234, where H = MMBtu/hr input rating of the unit
| Fuel Burning Equipment - 05/14/70 - 12/31/84 | PM | ≥ 250 | MMBtu/hr | Any | 0.1 | lb/MMBtu | Env-A 2002.07(c)(3)
| Fuel Burning Equipment - Post-01/01/85 | PM | < 100 | MMBtu/hr | Any | 0.3 | lb/MMBtu | Env-A 2002.08(c)(1)
| Fuel Burning Equipment - Post-01/01/85 | PM | 100 - 249 | MMBtu/hr | Any | 0.15 | lb/MMBtu | Env-A 2002.08(c)(2)
| Fuel Burning Equipment - Post-01/01/85 | PM | ≥ 250 | MMBtu/hr | Any | 0.1 | lb/MMBtu | Env-A 2002.08(c)(3)
| Fuel Burning Equipment | SO2 | < 1,000 | MMBtu/hr | Any | 1.6 | lb/MMBtu | Env-A 403.01
| Fuel Burning Equipment | SO2 | All |  | Oil No. 2 | 0.4 | wt% sulfur | Env-A 1604.01(a)
| Fuel Burning Equipment | SO2 | All |  | Oil No. 4 | 1 | wt% sulfur | Env-A 1604.01(b)
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5 & 6 | 2.2 | wt% sulfur | Env-A 1604.01(a) | Coos County
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5 & 6 | 2 | wt% sulfur | Env-A 1604.01(a) | Rest of the State
| Fuel Burning Equipment - Pre-04/15/70 | SO2 | All |  | Coal | 2.8 | lb S/MMBtu | Env-A 1601.01(a)(1)
| Fuel Burning Equipment - Pre-04/15/70 | SO2 | All |  | Coal | 2 | lb S/MMBtu | Env-A 1601.01(a)(2)
| Fuel Burning Equipment - Post-04/15/70 | SO2 | All |  | Coal | 1.5 | lb S/MMBtu | Env-A 1601.01(b)(1)
| Fuel Burning Equipment - Post-04/15/70 | SO2 | All |  | Coal | 1 | lb S/MMBtu | Env-A 1601.01(b)(2)
| Utility Boiler - Wet Bottom - Tangential/Face | NOx | ≥ 50 | MMBtu/hr | Coal or Coal/Other | 1 | lb/MMBtu | Env-A 1211.03(c)(1)(a) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Wet Bottom - Cyclone < 320 MW | NOx | ≥ 50 | MMBtu/hr | Coal or Coal/Other | 0.92 | lb/MMBtu | Env-A 1211.03(c)(1)(b)(1) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Wet Bottom - Cyclone > 320 MW | NOx | ≥ 50 | MMBtu/hr | Coal or Coal/Other | 1.4 | lb/MMBtu | Env-A 1211.03(c)(1)(b)(2) | RACT - Daily Avg | Emissions averaging across units allowed | In addition to tons/day limit below | Alternate: Apply RACT (SNCR or better) | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Dry Bottom - Tangential | NOx | ≥ 50 | MMBtu/hr | Coal or Coal/Other | 0.38 | lb/MMBtu | Env-A 1211.03(c)(2)(a) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Dry Bottom - Face | NOx | ≥ 50 | MMBtu/hr | Coal or Coal/Other | 0.5 | lb/MMBtu | Env-A 1211.03(c)(2)(b) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Dry Bottom - Stoker | NOx | ≥ 50 | MMBtu/hr | Coal or Coal/Other | 0.3 | lb/MMBtu | Env-A 1211.03(c)(2)(c) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Tangential/Face | NOx | ≥ 50 | MMBtu/hr | Oil | 0.35 | lb/MMBtu | Env-A 1211.03(c)(3)(a) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Face | NOx | ≥ 50 | MMBtu/hr | Oil/NG | 0.25 | lb/MMBtu | Env-A 1211.03(c)(3)(b) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Tangential | NOx | ≥ 50 | MMBtu/hr | Oil/NG | 0.25 | lb/MMBtu | Env-A 1211.03(c)(3)(c) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Tangential/Face | NOx | ≥ 50 | MMBtu/hr | NG | 0.2 | lb/MMBtu | Env-A 1211.03(c)(4) | RACT - Hourly Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Moving Grate | NOx | ≥ 50 | MMBtu/hr | Wood or Wood/Oil | 0.33 | lb/MMBtu | Env-A 1211.03(c)(5)(a) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Stationary Grate | NOx | ≥ 50 | MMBtu/hr | Wood or Wood/Oil | 0.25 | lb/MMBtu | Env-A 1211.03(c)(5)(b) | RACT - Daily Avg | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Wet Bottom - Cyclone | NOx | ≥ 50 | MMBtu/hr | Coal or Coal/Other | 15.4 | tons/day | Env-A 1211.03(d)(1) |  | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Utility Boiler - Wet Bottom - Cyclone | NOx | ≥ 50 | MMBtu/hr | Other than Coal | 3.8 | tons/day | Env-A 1211.03(d)(2) |  | Emissions averaging across units allowed |  |  | Boilers at Cogen. plants or small (<30 MW) power plants are subject to Industrial Boiler limits
| Industrial Boiler - Dry Bottom - Tangential | NOx | 50 - 99 | MMBtu/hr | Coal or Coal/Oil | 0.38 | lb/MMBtu | Env-A 1211.05(c)(1)(a) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Dry Bottom - Face | NOx | 50 - 99 | MMBtu/hr | Coal or Coal/Oil | 0.5 | lb/MMBtu | Env-A 1211.05(c)(1)(b) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Dry Bottom - Stoker | NOx | 50 - 99 | MMBtu/hr | Coal or Coal/Oil | 0.3 | lb/MMBtu | Env-A 1211.05(c)(1)(c) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Tangential/Face | NOx | 50 - 99 | MMBtu/hr | DO | 0.12 | lb/MMBtu | Env-A 1211.05(c)(2)(a) | RACT - Hourly Avg | Emissions averaging across units allowed
| Industrial Boiler - Tangential/Face | NOx | 50 - 99 | MMBtu/hr | RO | 0.3 | lb/MMBtu | Env-A 1211.05(c)(2)(b) | RACT - Daily Avg | Emissions averaging across units allowed |  | Alternate: Apply RACT (LNB or better)
| Industrial Boiler - Tangential/Face | NOx | 50 - 99 | MMBtu/hr | DO/NG | 0.12 | lb/MMBtu | Env-A 1211.05(c)(3)(c)(1) | RACT - Hourly Avg | Emissions averaging across units allowed
| Industrial Boiler - Tangential/Face | NOx | 50 - 99 | MMBtu/hr | RO/NG | 0.3 | lb/MMBtu | Env-A 1211.05(c)(3)(c)(2) | RACT - Daily Avg | Emissions averaging across units allowed |  | Alternate: Apply RACT (LNB or better)
| Industrial Boiler | NOx | 50 - 99 | MMBtu/hr | NG | 0.1 | lb/MMBtu | Env-A 1211.05(c)(4) | RACT - Hourly Avg | Emissions averaging across units allowed |  | Alternate: Apply RACT (LNB or better)
| Industrial Boiler - Moving Grate | NOx | 50 - 99 | MMBtu/hr | Wood or Wood/Oil | 0.33 | lb/MMBtu | Env-A 1211.05(c)(5)(a) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Stationary Grate | NOx | 50 - 99 | MMBtu/hr | Wood or Wood/Oil | 0.25 | lb/MMBtu | Env-A 1211.05(c)(5)(b) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Wet Bottom - Tangential/Face | NOx | ≥ 100 | MMBtu/hr | Coal or Coal/Other | 1 | lb/MMBtu | Env-A 1211.05(d)(1)(a) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Wet Bottom - Cyclone | NOx | ≥ 100 | MMBtu/hr | Coal or Coal/Other | 0.92 | lb/MMBtu | Env-A 1211.05(d)(1)(b) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Dry Bottom - Tangential | NOx | ≥ 100 | MMBtu/hr | Coal or Coal/Oil | 0.38 | lb/MMBtu | Env-A 1211.05(d)(2)(a) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Dry Bottom - Face | NOx | ≥ 100 | MMBtu/hr | Coal or Coal/Oil | 0.5 | lb/MMBtu | Env-A 1211.05(d)(2)(b) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Dry Bottom - Stoker | NOx | ≥ 100 | MMBtu/hr | Coal or Coal/Oil | 0.3 | lb/MMBtu | Env-A 1211.05(d)(2)(c) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Tangential/Face | NOx | ≥ 100 | MMBtu/hr | Oil | 0.3 | lb/MMBtu | Env-A 1211.05(d)(3)(a) | RACT - Daily Avg | Emissions averaging across units allowed |  | Alternate: Apply RACT (LNB or better)
| Industrial Boiler - Face | NOx | ≥ 100 | MMBtu/hr | Oil/NG | 0.25 | lb/MMBtu | Env-A 1211.05(d)(3)(b) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Tangential | NOx | ≥ 100 | MMBtu/hr | Oil/NG | 0.25 | lb/MMBtu | Env-A 1211.05(d)(3)(c) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Tangential/Face | NOx | ≥ 100 | MMBtu/hr | NG | 0.1 | lb/MMBtu | Env-A 1211.05(d)(4) | RACT - Hourly Avg | Emissions averaging across units allowed |  | Alternate: Apply RACT (LNB or better)
| Industrial Boiler - Moving Grate | NOx | ≥ 100 | MMBtu/hr | Wood or Wood/Oil | 0.33 | lb/MMBtu | Env-A 1211.05(d)(5)(a) | RACT - Daily Avg | Emissions averaging across units allowed
| Industrial Boiler - Stationary Grate | NOx | ≥ 100 | MMBtu/hr | Wood or Wood/Oil | 0.25 | lb/MMBtu | Env-A 1211.05(d)(5)(b) | RACT - Daily Avg | Emissions averaging across units allowed
| Auxiliary Boiler | NOx | ≥ 50 | MMBtu/hr | Any | 0.2 | lb/MMBtu | Env-A 1211.12(c) | RACT - Daily Avg - Major Sources | Emissions averaging across units allowed
| Turbine - Combined or Regenerative Cycle | NOx | ≥ 25 | MMBtu/hr | NG | 42 | ppmvd | Env-A 1211.06(c)(1)(a) | RACT - Hourly Avg | Emissions averaging across units allowed | Corrected to 15% O2 | Equiv: 0.155 lb/MMBtu
| Turbine - Combined or Regenerative Cycle | NOx | ≥ 25 | MMBtu/hr | Oil | 65 | ppmvd | Env-A 1211.06(c)(1)(c) | RACT - Hourly Avg | Emissions averaging across units allowed | Corrected to 15% O2 | Equiv: 0.253 lb/MMBtu
| Turbine - Simple Cycle | NOx | ≥ 25 | MMBtu/hr | NG | 55 | ppmvd | Env-A 1211.06(c)(2)(a) | RACT - Hourly Avg | Emissions averaging across units allowed | Corrected to 15% O2 | Equiv: 0.203 lb/MMBtu
| Turbine - Simple Cycle | NOx | ≥ 25 | MMBtu/hr | Oil | 75 | ppmvd | Env-A 1211.06(c)(2)(b) | RACT - Hourly Avg | Emissions averaging across units allowed | Corrected to 15% O2 | Equiv: 0.292 lb/MMBtu
| Turbine - All - Post 05/27/1999 | NOx | ≥ 25 | MMBtu/hr | NG | 25 | ppmvd | Env-A 1211.06(d) | RACT - Hourly Avg | Emissions averaging across units allowed | Corrected to 15% O2 | Equiv: 0.092 lb/MMBtu
| Turbine - Peak Shaving | NOx | All |  | Any | 0.9 | lb/MMBtu | Env-A 1211.13(b) | RACT - Hourly Avg - Major Sources | Emissions averaging across units allowed
NJ | Fuel Burning Equipment | PM | All |  | Any | Table | lb/hr | 7:27-4.2(a) | Table lists maximum allowable emission rates (lb/hr) according to heat input (MMBtu/hr)
| Fuel Burning Equipment | PM | ≥ 200 | MMBtu/hr | Any | 0.1 | lb/MMBtu | 7:27-4.2(a) | Calculated from Table presented with regulation
| Fuel Burning Equipment | SO2 | All |  | Oil No. 2 & lighter | 0.2 | wt% sulfur | 7:27-9.2(a) & (b) | Zones 3, 4 & 6 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No. 2 & lighter | 0.3 | wt% sulfur | 7:27-9.2(a) & (b) | Zones 1, 2 & 5 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No.4 | 0.3 | wt% sulfur | 7:27-9.2(a) & (b) | Zones 3, 4 & 6 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No. 4 | 0.7 | wt% sulfur | 7:27-9.2(a) & (b) | Zones 2 & 5 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No. 4 | 2 | wt% sulfur | 7:27-9.2(a) & (b) | Zone 1 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5, 6, & higher | 0.3 | wt% sulfur | 7:27-9.2(a) & (b) | Zones 4 & 6 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5, 6, & higher | 0.5 | wt% sulfur | 7:27-9.2(a) & (b) | Zone 3 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5, 6, & higher | 1 | wt% sulfur | 7:27-9.2(a) & (b) | Zones 2 & 5 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5, 6, & higher | 2 | wt% sulfur | 7:27-9.2(a) & (b) | Zone 1 | Does not apply when limits of rule 7:27-9.2(c) are met
| Fuel Burning Equipment | SO2 | All |  | Oil No. 2 & lighter | 0.21 | lb/MMBtu | 7:27-9.2(c) | Zones 3, 4 & 6
| Fuel Burning Equipment | SO2 | All |  | Oil No. 2 & lighter | 0.32 | lb/MMBtu | 7:27-9.2(c) | Zones 1, 2 & 5
| Fuel Burning Equipment | SO2 | All |  | Oil No.4 | 0.32 | lb/MMBtu | 7:27-9.2(c) | Zones 3, 4 & 6
| Fuel Burning Equipment | SO2 | All |  | Oil No. 4 | 0.74 | lb/MMBtu | 7:27-9.2(c) | Zones 2 & 5
| Fuel Burning Equipment | SO2 | All |  | Oil No. 4 | 2.1 | lb/MMBtu | 7:27-9.2(c) | Zone 1
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5, 6, & higher | 0.32 | lb/MMBtu | 7:27-9.2(c) | Zones 4 & 6
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5, 6, & higher | 0.53 | lb/MMBtu | 7:27-9.2(c) | Zone 3
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5, 6, & higher | 1.05 | lb/MMBtu | 7:27-9.2(c) | Zones 2 & 5
| Fuel Burning Equipment | SO2 | All |  | Oil No. 5, 6, & higher | 2.1 | lb/MMBtu | 7:27-9.2(c) | Zone 1
| Utility Boiler - Wet Bottom - Tangential/Face | NOx | All |  | Coal | 1 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Wet Bottom - Cyclone | NOx | All |  | Coal | 0.6 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Dry Bottom - Tangential | NOx | All |  | Coal | 0.38 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Dry Bottom - Face | NOx | All |  | Coal | 0.45 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Dry Bottom - Cyclone | NOx | All |  | Coal | 0.55 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Tangential | NOx | All |  | Oil and/or Gas | 0.2 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Face | NOx | All |  | Oil and/or Gas | 0.28 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Cyclone | NOx | All |  | Oil and/or Gas | 0.43 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Tangential/Face | NOx | All |  | Gas Only | 0.2 | lb/MMBtu | 7:27-19.4(a)
| Utility Boiler - Cyclone | NOx | All |  | Gas Only | 0.43 | lb/MMBtu | 7:27-19.4(a)
| Stationary Simple Cycle Gas Turbine | NOx | ≥ 30 | MMBtu/hr | Oil | 0.4 | lb/MMBtu | 7:27-19.5(a) | Emissions averaging across units allowed
| Stationary Simple Cycle Gas Turbine | NOx | ≥ 30 | MMBtu/hr | Gas | 0.2 | lb/MMBtu | 7:27-19.5(a) | Emissions averaging across units allowed
| Stationary Combined Cycle Gas Turbine | NOx | ≥ 30 | MMBtu/hr | Oil | 0.35 | lb/MMBtu | 7:27-19.5(b) | Emissions averaging across units allowed
| Stationary Combined Cycle Gas Turbine | NOx | ≥ 30 | MMBtu/hr | Gas | 0.15 | lb/MMBtu | 7:27-19.5(b) | Emissions averaging across units allowed
| Stationary Regenerative Cycle Gas Turbine | NOx | ≥ 30 | MMBtu/hr | Oil | 0.35 | lb/MMBtu | 7:27-19.5(b) | Emissions averaging across units allowed
| Stationary Regenerative Cycle Gas Turbine | NOx | ≥ 30 | MMBtu/hr | Gas | 0.15 | lb/MMBtu | 7:27-19.5(b) | Emissions averaging across units allowed
| ICI Boiler or Other Indirect Heat Exchanger | NOx | >5 | MMBtu/hr | All | Tune-up |  | 7:27-19.7(g) | Effective 3/7/2007
| ICI Boiler or Other Indirect Heat Exchanger | NOx | 50-100 | MMBtu/hr | Natural Gas | 0.1 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler or Other Indirect Heat Exchanger | NOx | 50-100 | MMBtu/hr | #2 Fuel Oil | 0.12 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler or Other Indirect Heat Exchanger | NOx | 50-100 | MMBtu/hr | Refinery Fuel Gas | 0.2 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler or Other Indirect Heat Exchanger | NOx | 50-100 | MMBtu/hr | Other Liquid Fuels | 0.3 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Wet Bottom Tangential | NOx | 50-100 | MMBtu/hr | Coal | 1 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Wet Bottom Face | NOx | 50-100 | MMBtu/hr | Coal | 1 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Wet Bottom Cyclone | NOx | 50-100 | MMBtu/hr | Coal | 0.55 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Dry Bottom Tangential | NOx | 50-100 | MMBtu/hr | Coal | 0.38 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Dry Bottom Face | NOx | 50-100 | MMBtu/hr | Coal | 0.43 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Dry Bottom Cyclone | NOx | 50-100 | MMBtu/hr | Coal | 0.55 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler or Other Indirect Heat Exchanger | NOx | 100+ | MMBtu/hr | Natural Gas Only | 0.1 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler or Other Indirect Heat Exchanger | NOx | 100+ | MMBtu/hr | Refinery Fuel Gas | 0.2 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Tangential | NOx | 100+ | MMBtu/hr | Fuel oil and/or natural gas | 0.2 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Face | NOx | 100+ | MMBtu/hr | Fuel oil and/or natural gas | 0.28 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Cyclone | NOx | 100+ | MMBtu/hr | Fuel oil and/or natural gas | 0.43 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Wet Bottom Tangential | NOx | 100+ | MMBtu/hr | Coal | 1 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Wet Bottom Face | NOx | 100+ | MMBtu/hr | Coal | 1 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Wet Bottom Cyclone | NOx | 100+ | MMBtu/hr | Coal | 0.6 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Dry Bottom Tangential | NOx | 100+ | MMBtu/hr | Coal | 0.38 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Dry Bottom Face | NOx | 100+ | MMBtu/hr | Coal | 0.45 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| ICI Boiler Dry Bottom Cyclone | NOx | 100+ | MMBtu/hr | Coal | 0.55 | lb/MMBtu | 7:72-19.7(h) | Effective 3/7/2007
| Non-Utility Boiler - Wet Bottom - Tangential/Face | NOx | 20 - 100 | MMBtu/hr | Coal | 1 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Wet Bottom - Cyclone | NOx | 20 - 100 | MMBtu/hr | Coal | 0.55 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Dry Bottom - Tangential | NOx | 20 - 100 | MMBtu/hr | Coal | 0.38 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Dry Bottom - Face | NOx | 20 - 100 | MMBtu/hr | Coal | 0.43 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Dry Bottom - Cyclone | NOx | 20 - 100 | MMBtu/hr | Coal | 0.55 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Tangential/Face/Cyclone | NOx | 20 - 100 | MMBtu/hr | Oil No. 2 | 0.12 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Tangential/Face/Cyclone | NOx | 20 - 100 | MMBtu/hr | Other Liquid Fuels | 0.3 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Tangential/Face | NOx | 20 - 100 | MMBtu/hr | Refinery Fuel Gas | 0.2 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Tangential/Face/Cyclone | NOx | 20 - 100 | MMBtu/hr | Natural Gas | 0.1 | lb/MMBtu | 7:27-19.6(a) & (b)
| Non-Utility Boiler - Wet Bottom - Tangential/Face | NOx | ≥ 100 | MMBtu/hr | Coal | 1 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Wet Bottom - Cyclone | NOx | ≥ 100 | MMBtu/hr | Coal | 0.6 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Dry Bottom - Tangential | NOx | ≥ 100 | MMBtu/hr | Coal | 0.38 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Dry Bottom - Face | NOx | ≥ 100 | MMBtu/hr | Coal | 0.45 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Dry Bottom - Cyclone | NOx | ≥ 100 | MMBtu/hr | Coal | 0.55 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Tangential | NOx | ≥ 100 | MMBtu/hr | Oil and/or Gas | 0.2 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Face | NOx | ≥ 100 | MMBtu/hr | Oil and/or Gas | 0.28 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Cyclone | NOx | ≥ 100 | MMBtu/hr | Oil and/or Gas | 0.43 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Tangential/Face | NOx | ≥ 100 | MMBtu/hr | Refinery Fuel Gas | 0.2 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Tangential/Face | NOx | ≥ 100 | MMBtu/hr | Gas Only | 0.2 | lb/MMBtu | 7:27-19.6(c)
| Non-Utility Boiler - Cyclone | NOx | ≥ 100 | MMBtu/hr | Gas Only | 0.43 | lb/MMBtu | 7:27-19.6(c)
NY | Fuel Burning Equipment | PM | > 250 | MMBtu/hr | Liquid fuel from coal | 0.1 | lb/MMBtu | 227-1.2(a)(1)
| Fuel Burning Equipment | PM | 50 - 250 | MMBtu/hr | Liquid fuel from coal | 0.2 | lb/MMBtu | 227-1.2(a)(2)
| Fuel Burning Equipment | PM | > 250 | MMBtu/hr | Coal, wood, coke, etc. | 0.1 | lb/MMBtu | 227-1.2(a)(3) | Units with permits to construct submitted after August 11, 1972.
| Fuel Burning Equipment | PM | All | MMBtu/hr | Coal, wood, coke, etc. | Formula | lb/MMBtu | 227-1.2(b) | Based on a formula: E (lb/MMBtu) = 1.0/p0.22, where p = max heat input capacity (MMBtu/hr) |  | Applies to units not subject to 227-1.2(a)(3)
| Fuel Burning Equipment - Spreader Stokers | PM | ≤ 300 | MMBtu/hr | Coal, wood, coke, etc. | 0.6 | lb/MMBtu | 227-1.2(c)(1) | Units in operation prior to June 1, 1972
| Fuel Burning Equipment - All others | PM | ≤ 300 | MMBtu/hr | Coal, wood, coke, etc. | Table | lb/MMBtu | 227-1.2(c)(2) | Table lists maximum allowable emission rates (lb/hr) according to heat input (MMBtu/hr): 1-100 MMBtu/hr = 0.6 lb/MMBtu; 200 MMBtu/hr = 0.45 lb/MMBtu; 300 MMBtu/hr = 0.30 lb/MMBtu (interpolate for units with heat input capacities not shown)
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Oil | 0.75 | wt% sulfur | 225-1.2(a)(1) | Applies when the permit to construct was received after March 15, 1973, and the installation is not located in New York City, Nassau, Rockland, or Westchester Counties.
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Coal | 0.6 | lb S/MMBtu | 225-1.2(a)(1) | Applies when the permit to construct was received after March 15, 1973, and the installation is not located in New York City, Nassau, Rockland, or Westchester Counties.
| Fuel Burning Equipment | SO2 | All |  | Residual Oil | 0.3 | wt% sulfur | 225-1.2(d) | New York City | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Distillate Oil | 0.2 | wt% sulfur | 225-1.2(d) | New York City | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Coal | 0.2 | lb S/MMBtu | 225-1.2(d) | New York City | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Oil | 0.37 | wt% sulfur | 225-1.2(d) | Nassau, Rockland, and Westchester Counties | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Coal | 0.2 | lb S/MMBtu | 225-1.2(d) | Nassau, Rockland, and Westchester Counties | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Oil | 1 | wt% sulfur | 225-1.2(d) | Suffold County: Towns of Babylon, Brookhaven, Huntington, Islip, and Smith Town | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Coal | 0.6 | lb S/MMBtu | 225-1.2(d) | Suffold County: Towns of Babylon, Brookhaven, Huntington, Islip, and Smith Town | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Oil | 1.1 | wt% sulfur | 225-1.2(d) | Erie County: City of Lackawana and South Buffalo | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Coal | 1.7 | lb S/MMBtu | 225-1.2(d) | Erie County: City of Lackawana and South Buffalo | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Oil | 1.5 | wt% sulfur | 225-1.2(d) | Niagara County and remainder of Erie County | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Coal | 1.7 | lb S/MMBtu | 225-1.2(d) | Niagara County and remainder of Erie County | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Oil | 1.5 | wt% sulfur | 225-1.2(d) | Remainder of State | Effective January 1, 1988
| Fuel Burning Equipment | SO2 | All |  | Coal | 2.5 | lb S/MMBtu | 225-1.2(d) | Remainder of State | Effective January 1, 1988
| Very Large Boilers - Tangential/Wall | NOx | > 250 | MMBtu/hr | Gas Only | 0.2 | lb/MMBtu | 227-2.4(a)(1) | RACT - 24hr average | From October 1 to April 30th, 30-day rolling avg allowed
| Very Large Boilers - Tangential/Wall | NOx | > 250 | MMBtu/hr | Gas/Oil | 0.25 | lb/MMBtu | 227-2.4(a)(1) | RACT - 24hr average | From October 1 to April 30th, 30-day rolling avg allowed
| Very Large Boilers - Cyclone | NOx | > 250 | MMBtu/hr | Gas/Oil | 0.43 | lb/MMBtu | 227-2.4(a)(1) | RACT - 24hr average | From October 1 to April 30th, 30-day rolling avg allowed
| Very Large Boilers - Wet Bottom - Tangential/Wall | NOx | > 250 | MMBtu/hr | Coal | 1 | lb/MMBtu | 227-2.4(a)(1) | RACT - 24hr average | From October 1 to April 30th, 30-day rolling avg allowed
| Very Large Boilers - Wet Bottom - Cyclone | NOx | > 250 | MMBtu/hr | Coal | 0.6 | lb/MMBtu | 227-2.4(a)(1) | RACT - 24hr average | From October 1 to April 30th, 30-day rolling avg allowed
| Very Large Boilers - Dry Bottom - Tangential | NOx | > 250 | MMBtu/hr | Coal | 0.42 | lb/MMBtu | 227-2.4(a)(1) | RACT - 24hr average | From October 1 to April 30th, 30-day rolling avg allowed
| Very Large Boilers - Dry Bottom - Wall | NOx | > 250 | MMBtu/hr | Coal | 0.45 | lb/MMBtu | 227-2.4(a)(1) | RACT - 24hr average | From October 1 to April 30th, 30-day rolling avg allowed
| Very Large Boilers - Dry Bottom - Stoker | NOx | > 250 | MMBtu/hr | Coal | 0.3 | lb/MMBtu | 227-2.4(a)(1) | RACT - 24hr average | From October 1 to April 30th, 30-day rolling avg allowed | Emission limit is 0.33 lb/MMBtu when at least 25% of other solid fuels are burned on a Btu basis
| Large Boilers | NOx | 100 - 250 | MMBtu/hr | Gas Only | 0.2 | lb/MMBtu | 227-2.4(b)(1) | RACT - 1hr avg, or 24hr avg if a CEMS is used
| Large Boilers | NOx | 100 - 250 | MMBtu/hr | Gas/Oil | 0.3 | lb/MMBtu | 227-2.4(b)(1) | RACT - 1hr avg, or 24hr avg if a CEMS is used
| Large Boilers | NOx | 100 - 250 | MMBtu/hr | Pulverized Coal | 0.5 | lb/MMBtu | 227-2.4(b)(1) | RACT - 1hr avg, or 24hr avg if a CEMS is used
| Large Boilers | NOx | 100 - 250 | MMBtu/hr | Coal (Overfeed Stoker) | 0.3 | lb/MMBtu | 227-2.4(b)(1) | RACT - 1hr avg, or 24hr avg if a CEMS is used | Emission limit is 0.33 lb/MMBtu when at least 25% of other solid fuels are burned on a Btu basis
| Mid-size Boilers | NOx | 50 - 100 | MMBtu/hr | Natural Gas | 0.1 | lb/MMBtu | 227-2.4(c)(2) | RACT - 1hr avg, or 24hr avg if a CEMS is used | Must utilize low NOx burners
| Mid-size Boilers | NOx | 50 - 100 | MMBtu/hr | Distillate Oil | 0.12 | lb/MMBtu | 227-2.4(c)(2) | RACT - 1hr avg, or 24hr avg if a CEMS is used | Must utilize low NOx burners
| Mid-size Boilers | NOx | 50 - 100 | MMBtu/hr | Residual Oil | 0.3 | lb/MMBtu | 227-2.4(c)(2) | RACT - 1hr avg, or 24hr avg if a CEMS is used | Must utilize low NOx burners with flue gas recirculation
| Combustion Turbine - Simple Cycle/Regenerative | NOx | > 10 | MMBtu/hr | Gas Only | 50 | ppmvd | 227-2.4(e)(1)(i) | RACT - 1hr avg, or 24hr avg if a CEMS is used | Turbine operates < 500 hrs between October 1st and April 30th
| Combustion Turbine - Simple Cycle/Regenerative | NOx | > 10 | MMBtu/hr | Multiple Fuels | 100 | ppmvd | 227-2.4(e)(1)(ii) | RACT - 1hr avg, or 24hr avg if a CEMS is used | Turbine operates < 500 hrs between October 1st and April 30th
| Combustion Turbine - Combined Cycle | NOx | > 10 | MMBtu/hr | Gas | 42 | ppmvd | 227-2.4(e)(2)(i) | RACT - 1hr avg, or 24hr avg if a CEMS is used
| Combustion Turbine - Combined Cycle | NOx | > 10 | MMBtu/hr | Oil | 65 | ppmvd | 227-2.4(e)(2)(ii) | RACT - 1hr avg, or 24hr avg if a CEMS is used
PA | Fuel Burning Equipment | PM | 2.5 - 50 | MMBtu/hr | All | 0.4 | lb/MMBtu | 123.11(a)(1)
| Fuel Burning Equipment | PM | 50 - 600 | MMBtu/hr | All | Formula | lb/MMBtu | 123.11(a)(2) | Based on a formula: A (lb/MMBtu) = 3.6 E-0.56, where E = MMBtu/hr input rating of the unit
| Fuel Burning Equipment | PM | > 600 | MMBtu/hr | All | 0.1 | lb/MMBtu | 123.11(a)(3)
| Fuel Burning Equipment | SO2 | All |  | All | 4 | lb/MMBtu | 123.22(a)(1) | Nonair basin areas | As measured over a 1-hr period
| Fuel Burning Equipment | SO2 | All |  | No. 2 Oil & lighter | 0.5 | wt% sulfur | 123.22(a)(2) | Nonair basin areas
| Fuel Burning Equipment | SO2 | All |  | No. 4, 5, 6, & heavier | 2.8 | wt% sulfur | 123.22(a)(2) | Nonair basin areas
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 3.7 | lb/MMBtu | 123.22(a)(4)(iii) | Nonair basin areas | 30-day running average
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 4 | lb/MMBtu | 123.22(a)(4)(iii) | Nonair basin areas | Daily average, not to be exceeded more than 2 days in any 30-day running period
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 4.8 | lb/MMBtu | 123.22(a)(4)(iii) | Nonair basin areas | Daily maximum average
| Fuel Burning Equipment | SO2 | All |  | All | 4 | lb/MMBtu | 123.22(b)(1) | As measured over a 1-hr period | Erie, Harrisburg, York, Lancaster, Scranton, Wilkes-Barre air basins
| Fuel Burning Equipment | SO2 | All |  | No. 2 Oil & lighter | 0.3 | wt% sulfur | 123.22(b)(2) | Erie, Harrisburg, York, Lancaster, Scranton, Wilkes-Barre air basins
| Fuel Burning Equipment | SO2 | All |  | No. 4, 5, 6, & heavier | 2.8 | wt% sulfur | 123.22(b)(2) | Erie, Harrisburg, York, Lancaster, Scranton, Wilkes-Barre air basins
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 3.7 | lb/MMBtu | 123.22(b)(4)(iii) | 30-day running average | Erie, Harrisburg, York, Lancaster, Scranton, Wilkes-Barre air basins
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 4 | lb/MMBtu | 123.22(b)(4)(iii) | Daily average, not to be exceeded more than 2 days in any 30-day running period | Erie, Harrisburg, York, Lancaster, Scranton, Wilkes-Barre air basins
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 4.8 | lb/MMBtu | 123.22(b)(4)(iii) | Daily maximum average | Erie, Harrisburg, York, Lancaster, Scranton, Wilkes-Barre air basins
| Fuel Burning Equipment | SO2 | All |  | All | 3 | lb/MMBtu | 123.22(c)(1) | As measured over a 1-hr period | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstwon air basins
| Fuel Burning Equipment | SO2 | All |  | No. 2 Oil & lighter | 0.3 | wt% sulfur | 123.22(c)(2) | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstwon air basins
| Fuel Burning Equipment | SO2 | All |  | No. 4, 5, 6, & heavier | 2 | wt% sulfur | 123.22(c)(2) | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstwon air basins
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 2.8 | lb/MMBtu | 123.22(c)(4)(iii) | 30-day running average | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstwon air basins
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 3 | lb/MMBtu | 123.22(c)(4)(iii) | Daily average, not to be exceeded more than 2 days in any 30-day running period | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstwon air basins
| Fuel Burning Equipment | SO2 | > 250 | MMBtu/hr | Solid fossil fuel | 3.6 | lb/MMBtu | 123.22(c)(4)(iii) | Daily maximum average | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstwon air basins
| Fuel Burning Equipment | SO2 | 2.5 - 50 | MMBtu/hr | All | 1 | lb/MMBtu | 123.22(d)(1) | Allegheny County, Lower Beaver Valley, and Monongahela Valley air basins
| Fuel Burning Equipment | SO2 | 50 - 2,000 | MMBtu/hr | All | Formula | lb/MMBtu | 123.22(d)(2) | Allegheny County, Lower Beaver Valley, and Monongahela Valley air basins |  | Based on a formula: A (lb/MMBtu) = 1.7 E-0.14, where E = MMBtu/hr input rating of the unit
| Fuel Burning Equipment | SO2 | > 2,000 | MMBtu/hr | All | 0.6 | lb/MMBtu | 123.22(d)(3) | Allegheny County, Lower Beaver Valley, and Monongahela Valley air basins
| Fuel Burning Equipment | SO2 | < 250 | MMBtu/hr | All | 1.00 / 1.20 | lb/MMBtu | 123.22(e)(1) | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | ≥ 250 | MMBtu/hr | All | 0.60 / 1.20 | lb/MMBtu | 123.22(e)(1) | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | All |  | No. 2 Oil & lighter | 0.20 / 0.30 | wt% sulfur | 123.22(e)(2) | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | All |  | No. 4, 5, 6, & heavier | 0.50 / 1.00 | wt% sulfur | 123.22(e)(2) | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | All |  | Noncommercial fuel | 0.60 / 1.20 | lb/MMBtu | 123.22(e)(3) | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | < 250 | MMBtu/hr | Solid fossil fuel | 0.75 / 0.90 | lb/MMBtu | 123.22(e)(5)(iii) | 30-day running average | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | ≥ 250 | MMBtu/hr | Solid fossil fuel | 0.45 / 0.90 | lb/MMBtu | 123.22(e)(5)(iii) | 30-day running average | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | < 250 | MMBtu/hr | Solid fossil fuel | 1.00 / 1.20 | lb/MMBtu | 123.22(e)(5)(iii) | Daily average, not to be exceeded more than 2 days in any 30-day running period | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | ≥ 250 | MMBtu/hr | Solid fossil fuel | 0.60 / 1.20 | lb/MMBtu | 123.22(e)(5)(iii) | Daily average, not to be exceeded more than 2 days in any 30-day running period | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | < 250 | MMBtu/hr | Solid fossil fuel | 1.20 / 1.44 | lb/MMBtu | 123.22(e)(5)(iii) | Daily maximum average | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | SO2 | ≥ 250 | MMBtu/hr | Solid fossil fuel | 0.72 / 1.44 | lb/MMBtu | 123.22(e)(5)(iii) | Daily maximum average | Inner Zone / Outer Zone | Southeast Pennsylvania air basin
| Fuel Burning Equipment | NOx | 100 - 250 | MMBtu/hr | NG or noncommercial gas | 0.1 | lb/MMBtu | 129.201(c)(1)(i)
| Fuel Burning Equipment | NOx | 100 - 250 | MMBtu/hr | Solid or liquid fuel | 0.2 | lb/MMBtu | 129.201(c)(1)(ii)
RI | Steam or Hot Water Generating Units | PM | > 1 | MMBtu/hr | fossil fuel | 0.1 | lb/MMBtu | 13.2.1
| Fuel Burning Equipment | SO2 | All |  | All | 1.1 | lb/MMBtu | 8.3.1
| Fuel Burning Equipment | SO2 | ≥ 250 | MMBtu/hr | Coal | 1.21 | lb/MMBtu | 8.3.4.1(a) & (b) | Provided source does not exceed limit within any 30-day period
| Fuel Burning Equipment | SO2 | ≥ 250 | MMBtu/hr | Coal | 2.31 | lb/MMBtu | 8.3.4.1(a) & (b) | Provided source does not exceed limit within any 24-hr period
| Utility Boilers | NOx | All |  | NG or LPG | 0.2 | lb/MMBtu | 27.4.1(a)
| Utility Boilers | NOx | All |  | fuel oil | 0.25 | lb/MMBtu | 27.4.1(b)
| Industrial, Commercial, Institutional Boilers | NOx | > 50 | MMBtu/hr | Natural Gas | 0.1 | lb/MMBtu | 27.4.2(a)(1)
| Industrial, Commercial, Institutional Boilers | NOx | > 50 | MMBtu/hr | Distillate oil or LPG | 0.12 | lb/MMBtu | 27.4.2(a)(2)
VT | Fuel Burning Equipment | PM | ≤ 10 | MMBtu/hr | fossil fuel | 0.5 | lb/MMBtu | 5-231(3)(a)(i)
| Fuel Burning Equipment | PM | 10 - 250 | MMBtu/hr | fossil fuel | Formula | lb/MMBtu | 5-231(3)(a)(ii) | Based on formula: E=10[-0.47039x(logHI)+0.16936], where E is the emission limit in lb/MMBtu, and HI is the heat input in MMBtu/hr
| Fuel Burning Equipment | PM | 250 - 1,000 | MMBtu/hr | fossil fuel | 0.1 | lb/MMBtu | 5-231(3)(a)(iii)
| Fuel Burning Equipment | PM | > 1,000 | MMBtu/hr | fossil fuel | 0.06 | lb/MMBtu | 5-231(3)(a)(iv)
| Fuel Burning Equipment | PM | > 90 | HP | wood fuel | 0.45 | gr/dscf | 5-231(3)(b)(i) | Corrected to 12% CO2 | Installed & commenced operation before December 5, 1977.
| Fuel Burning Equipment | PM | 90 - 1,300 | HP | wood fuel | 0.2 | gr/dscf | 5-231(3)(b)(ii) | Corrected to 12% CO2 | Installed & commenced operation after December 5, 1977.
| Fuel Burning Equipment | PM | ≥ 1,300 | HP | wood fuel | 0.1 | gr/dscf | 5-231(3)(b)(iii) | Corrected to 12% CO2 | Installed & commenced operation after December 5, 1977.
| Fuel Burning Equipment | SO2 | ≥ 250 | MMBtu/hr | liquid fossil fuel | 0.8 | lb/MMBtu | 5-252(1)(a)
| Fuel Burning Equipment | SO2 | ≥ 250 | MMBtu/hr | Solid fossil fuel | 1.2 | lb/MMBtu | 5-252(1)(b)
| Fuel Burning Equipment | NOx | ≥ 250 | MMBtu/hr | gaseous fossil fuel | 0.2 | lb/MMBtu | 5-251(1)(a)
| Fuel Burning Equipment | NOx | ≥ 250 | MMBtu/hr | liquid fossil fuel | 0.3 | lb/MMBtu | 5-251(1)(b)
| Fuel Burning Equipment | NOx | ≥ 250 | MMBtu/hr | Solid fossil fuel | 0.7 | lb/MMBtu | 5-251(1)(c)
BAAQMD | Fuel Burning Equipment | PM | All |  | All | 0.15 | gr/dscf | 6-310 | Corrected to 12% CO2 for incineration devices
| Fuel Burning Equipment | SO2 | All |  | Liquid or solid fuel | 0.5 | wt% sulfur | 9-1-304
| Fuel Burning Equipment | SO2 | All |  | Liquid or solid fuel | 300 | ppmvd | 9-1-304
| EGU Boilers | NOx | ≥ 1,750 | MMBtu/hr | Gaseous fuel | 10 | ppmvd | 9-11-301.1 | Corrected to 3% O2
| EGU Boilers | NOx | ≥ 1,750 | MMBtu/hr | Non-gaseous fuel | 25 | ppmvd | 9-11-301.2 | Corrected to 3% O2
| EGU Boilers | NOx | 1,500 - 1,750 | MMBtu/hr | Gaseous fuel | 25 | ppmvd | 9-11-303.1 | Corrected to 3% O2
| EGU Boilers | NOx | 1,500 - 1,750 | MMBtu/hr | Non-gaseous fuel | 110 | ppmvd | 9-11-303.2 | Corrected to 3% O2
| EGU Boilers | NOx | < 1,500 | MMBtu/hr | Gaseous fuel | 30 | ppmvd | 9-11-305.1 | Corrected to 3% O2
| EGU Boilers | NOx | < 1,500 | MMBtu/hr | Non-gaseous fuel | 110 | ppmvd | 9-11-305.2 | Corrected to 3% O2
| EGU System | NOx | All |  | All | 0.28 | lb/MMBtu | 9-11-308 | Calculated each operating day as the average of all hourly data for the preceeding 30 operating days
| EGU System - plant wide | NOx | All |  | Gaseous fuel | 0.018 | lb/MMBtu | 9-11-309.1 | Advanced Technology Alternative Emission Control Plan
| Boilers, Steam Generators, or process heaters | NOx | ≥ 10 | MMBtu/hr | Gaseous fuel | 30 | ppmvd | 9-7-301.1 | Corrected to 3% O2
| Boilers, Steam Generators, or process heaters | NOx | ≥ 10 | MMBtu/hr | Non-gaseous fuel | 40 | ppmvd | 9-7-302.1 | Corrected to 3% O2
| Boilers, Steam Generators, or process heaters | NOx | ≥ 10 | MMBtu/hr | Non-gaseous fuel | 150 | ppmvd | 9-7-305.1 | Corrected to 3% O2 | Limit applies during natural gas curtailment periods, when gaseous fuels are unavailable.
SCAQMD | Fuel Burning Equipment | PM | All |  | All | 0.1 | gr/scf | Rule 409 | Corrected to 12% CO2, averaged over a minimum of 15 consecutive minutes.
| Fuel Burning Equipment | SO2 | All |  | Natural Gas | 16 | ppmv | 431.1(c)(1) | Sulfur content of natural gas calculated as H2S
| Fuel Burning Equipment | SO2 | All |  | Other Gaseous fuel | 40 | ppmv | 431.1(c)(2) | Sulfur content of natural gas calculated as H2S, and averaged over a 4-hr period
| Fuel Burning Equipment | SO2 | All |  | Liquid Fuel | 500 | ppmw | 431.2(d)(1) | Sulfur content of liquid fuel is measured by weight
| Fuel Burning Equipment | SO2 | All |  | Low Sulfur Diesel | 15 | ppmw | 431.2(d)(2) | Sulfur content of low sulfur diesel is measured by weight
| Fuel Burning Equipment | SO2 | All |  | Solid fossil fuel | 0.56 | lb/MMBtu | 431.3(a)
| Non-mobile fuel burning equipment | NOx | 555 - 1,786 | MMBtu/hr | Gas fuel | 300 | ppmvd | 474(a) | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Non-mobile fuel burning equipment | NOx | 555 - 1,786 | MMBtu/hr | Liquid or solid fuel | 400 | ppmvd | 474(a) | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Non-mobile fuel burning equipment | NOx | 1,786 - 2,143 | MMBtu/hr | Gas fuel | 225 | ppmvd | 474(a) | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Non-mobile fuel burning equipment | NOx | 1,786 - 2,143 | MMBtu/hr | Liquid or solid fuel | 325 | ppmvd | 474(a) | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Non-mobile fuel burning equipment | NOx | > 2,143 | MMBtu/hr | Gas fuel | 125 | ppmvd | 474(a) | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Non-mobile fuel burning equipment | NOx | > 2,173 | MMBtu/hr | Liquid or solid fuel | 225 | ppmvd | 474(a) | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Steam Generating Equipment | NOx | > 555 | MMBtu/hr | Gas fuel | 125 | ppmvd | 474(b) | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Steam Generating Equipment | NOx | > 555 | MMBtu/hr | Liquid or solid fuel | 225 | ppmvd | 474(b) | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Supercritical Steam Generating Unit | NOx | > 2,143 | MMBtu/hr | All | 400 | ppmvd | 474(d) | During pressure ramp periods of boiler startups. | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Steam Generating Equipment | NOx | > 50 | MMBtu/hr | Gas fuel | 125 | ppmvd | 476(a)(1) | Applies to units installed after May 7, 1976 | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Steam Generating Equipment | NOx | > 50 | MMBtu/hr | Liquid or solid fuel | 225 | ppmvd | 476(a)(1) | Applies to units installed after May 7, 1976 | Corrected to 3% O2, averaged over a minimum of 15 consecutive minutes
| Existing Stationary Gas Turbines | NOx | ≥ 0.3 | MW | All | Formula |  | 1134(c)(1) | Applies to units installed as of August 4, 1989. | Based on a formula: Compliance Limit = Reference Limit x (EFF/25%), where Reference Limits are the NOx limit, based on unit capacity, and EFF is the unit's demonstrated efficiency
| Electric Power Generating Systems | NOx | All |  | All | 0.15 | lb/MWH | 1135(c)(1) | Applies to Souther California Edison power plant
| Electric Power Generating Systems | NOx | All |  | All | 0.15 | lb/MWH | 1135(c)(2) | Applies to Los Angeles Department of Water & Power
| Electric Power Generating Systems | NOx | All |  | All | 0.2 | lb/MWH | 1135(c)(3) | Applies to the Cities of Burbank, Glendale, and Pasedena
| Boilers, Steam Generators, and process heaters | NOx | 2 - 5 | MMBtu/hr | All | 0.037 | lb/MMBtu | 1146.1(c)(1) | Alternate limit is 30 ppm NOx.
| Small Industrial Boilers | NOx | 0.75 - 2 | MMBtu/hr | Natural Gas | 0.037 | lb/MMBtu | 1146.2(c)(1) | Alternate limit is 30 ppmvd NOx, corrected to 3% O2
| ICI Boilers, Steam Generators, Process Heaters | NOx | > 40 | MMBtu/hr | All | 0.036 | lb/MMBtu | 1146(c)(1) | Alternate limit is 30 ppm NOx.
| ICI Boilers, Steam Generators, Process Heaters | NOx | ≥ 5 | MMBtu/hr | Non-gaseous fuel | 0.052 | lb/MMBtu | 1146(c)(2)(A) | Alternate limit is 40 ppm NOx.
| ICI Boilers, Steam Generators, Process Heaters | NOx | 5 - 40 | MMBtu/hr | All | 0.052 | lb/MMBtu | 1146(c)(2)(B) | Alternate limit is 40 ppm NOx.
| ICI Boilers, Steam Generators, Process Heaters | NOx | ≥ 10 | MMBtu/hr | Gaseous fuel | 0.036 | lb/MMBtu | 1146(c)(3)(A) | Alternate limit is 30 ppm NOx.
| ICI Boilers, Steam Generators, Process Heaters | NOx | 5 - 40 | MMBtu/hr | All | 0.036 | lb/MMBtu | 1146(c)(3)(B) | Alternate limit is 30 ppm NOx. | Weighted average calculated when burning a combination of gaseous and non-gaseous fuels.
SJVAPCD | Fuel Burning Equipment | PM | All |  | All | 0.1 | gr/dscf | Rule 4301, 5.1 | Corrected to 12% CO2
| Fuel Burning Equipment | PM | All |  | All | Formula |  | Rule 4202, 4 | Based on formula: E = 3.59P0.62, where P is ≤ 30 tons/hr, or E = 17.31P0.16, where P > 30 tons/hr. E is the allowable emission rate in lb/hr, while P is the process weight rate in tons/hr.
| Fuel Burning Equipment | SO2 | All |  | All | 200 | lb/hr | Rule 4301, 5.2.1
| Existing Steam Generator | SO2 | ≥ 15 | MMBtu/hr | All | 0.11 | lb/MMBtu | Rule 4406, 4.2 | Applies to units in Kern County
| Fuel Burning Equipment | NOx | All |  | All | 140 | lb/hr | Rule 4301, 5.2.2
| Boilers, Steam Generators, and Process Heaters | NOx | > 9 | MMBtu/hr | Gaseous fuel | 0.1 | lb/MMBtu | Rule 4351, 5.1 | Alternate limit is 95 ppmvd at 3% O2 | Applies to all units except those with natural or induced drafts |  | Does not apply to units located west of Interstate 5 located in Fresno, Kern, or Kings county.
| Boilers, Steam Generators, and Process Heaters | NOx | > 9 | MMBtu/hr | Distillate Oil | 0.15 | lb/MMBtu | Rule 4351, 5.1 | Alternate limit is 115 ppmvd at 3% O2 | Applies to all units except those with natural or induced drafts |  | Does not apply to units located west of Interstate 5 located in Fresno, Kern, or Kings county.
| Boilers, Steam Generators, and Process Heaters | NOx | > 9 | MMBtu/hr | Residual or Crude Oil | 0.22 | lb/MMBtu | Rule 4351, 5.1 | Alternate limit is 165 ppmvd at 3% O2 | Applies to all units except those with natural or induced drafts |  | Does not apply to units located west of Interstate 5 located in Fresno, Kern, or Kings county.
| Boilers, Steam Generators, and Process Heaters | NOx | > 9 | MMBtu/hr | Gaseous fuel | 0.18 | lb/MMBtu | Rule 4351, 5.1 | Alternate limit is 147 ppmvd at 3% O2 | Applies to units with natural and induced drafts | Does not apply to units located west of Interstate 5 located in Fresno, Kern, or Kings county.
| Boilers, Steam Generators, and Process Heaters | NOx | > 9 | MMBtu/hr | Distillate Oil | 0.2 | lb/MMBtu | Rule 4351, 5.1 | Alternate limit is 155 ppmvd at 3% O2 | Applies to units with natural and induced drafts | Does not apply to units located west of Interstate 5 located in Fresno, Kern, or Kings county.
| Boilers, Steam Generators, and Process Heaters | NOx | > 9 | MMBtu/hr | Residual or Crude Oil | 0.25 | lb/MMBtu | Rule 4351, 5.1 | Alternate limit is 194 ppmvd at 3% O2 | Applies to units with natural and induced drafts | Does not apply to units located west of Interstate 5 located in Fresno, Kern, or Kings county.
| Boilers, Steam Generators, and Process Heaters | NOx | > 9 | MMBtu/hr | Gaseous Fuel | 0.036 | lb/MMBtu | Rule 4351, 5.2.2.1 | Alternate limit is 30 ppmvd at 3% O2 | Alternate limit to section 5.1, for units not subject to sections 5.2.3 or 5.2.4, requiring compliance by May 31, 1997.
| Boilers, Steam Generators, and Process Heaters | NOx | > 9 | MMBtu/hr | Liquid Fuel | 0.052 | lb/MMBtu | Rule 4351, 5.2.2.2 | Alternate limit is 40 ppmvd at 3% O2 | Alternate limit to section 5.1, for units not subject to sections 5.2.3 or 5.2.4, requiring compliance by May 31, 1997.
| Boilers, Steam Generators, and Process Heaters | NOx | ≤ 40 | MMBtu/hr | Gaseous fuel | 0.085 | lb/MMBtu | Rule 4351, 5.2.3.1 | Alternate limit is 74 ppmvd at 3% O2 | Applies to units with natural and induced drafts | Alternate limit to section 5.1, requiring compliance by May 31, 1999.
| Boilers, Steam Generators, and Process Heaters | NOx | ≤ 40 | MMBtu/hr | Distillate Oil | 0.102 | lb/MMBtu | Rule 4351, 5.2.3.2 | Alternate limit is 78 ppmvd at 3% O2 | Applies to units with natural and induced drafts | Alternate limit to section 5.1, requiring compliance by May 31, 1999.
| Boilers, Steam Generators, and Process Heaters | NOx | ≤ 40 | MMBtu/hr | Residual or Crude Oil | 0.127 | lb/MMBtu | Rule 4351, 5.2.3.3 | Alternate limit is 97 ppmvd at 3% O2 | Applies to units with natural and induced drafts | Alternate limit to section 5.1, requiring compliance by May 31, 1999.
| Boilers, Steam Generators, and Process Heaters | NOx | ≤ 40 | MMBtu/hr | Gaseous Fuel | 0.061 | lb/MMBtu | Rule 4351, 5.2.4.1 | Alternate limit is 52 ppmvd at 3% O2 | Alternate limit to section 5.1, requiring compliance by May 31, 1999.
| Boilers, Steam Generators, and Process Heaters | NOx | ≤ 40 | MMBtu/hr | Liquid Fuel | 0.077 | lb/MMBtu | Rule 4351, 5.2.4.2 | Alternate limit is 59 ppmvd at 3% O2 | Alternate limit to section 5.1, requiring compliance by May 31, 1999.
| Boilers, Steam Generators, and Process Heaters | NOx | All |  | Solid Fuel | 200 | ppmv | Rule 4352, 5.1 | Applies to burning Municipal Solid Waste | Corrected to 12% CO2
| Boilers, Steam Generators, and Process Heaters | NOx | All |  | Solid Fuel | 0.35 | lb/MMBtu | Rule 4352, 5.1 | Applies to burning biomass using multiple hearth furnaces
| Boilers, Steam Generators, and Process Heaters | NOx | All |  | Solid Fuel | 0.2 | lb/MMBtu | Rule 4352, 5.1
| Existing Steam Generator | NOx | ≥ 35 | MMBtu/hr | Oil | 0.35 | lb/MMBtu | Rule 4405, 4.1.1 | Applies to generators operated by small producers | Applies to units in Central and Western Kern County
| Existing Steam Generator | NOx | ≥ 35 | MMBtu/hr | Oil | 0.2 | lb/MMBtu | Rule 4405, 4.1.2 | Applies to units in Central and Western Kern County
| Existing Steam Generator | NOx | 15 - 35 | MMBtu/hr | Oil | 0.38 | lb/MMBtu | Rule 4405, 4.1.3 | Applies to units in Central and Western Kern County
| Existing Steam Generator | NOx | ≥ 35 | MMBtu/hr | Natural Gas | 0.14 | lb/MMBtu | Rule 4405, 4.2.1 & 4.2.2 | Applies to units in Central and Western Kern County
| Existing Steam Generator | NOx | 15 - 35 | MMBtu/hr | Natural Gas | 0.18 | lb/MMBtu | Rule 4405, 4.2.3 | Applies to units in Central and Western Kern County
| Existing Steam Generator | NOx | All |  | Natural Gas | 0.02 | lb/MMBtu | Rule 4405, 5.1 | Alternate emission limit, for existing steam generators equipped with a "Coen" Low NOx Burner |  | Applies to units in Central and Western Kern County
| Boilers, Steam Generators, and Process Heaters | NOx | > 5 | MMBtu/hr | Gaseous fuel | 0.18 | lb/MMBtu | Rule 4305, 5.1.1 | Alternate limit is 147 ppmvd at 3% O2 | Applies to box or cabin type units, and vertical cylindrical process heaters
| Boilers, Steam Generators, and Process Heaters | NOx | > 5 | MMBtu/hr | Liquid fuel | 0.2 | lb/MMBtu | Rule 4305, 5.1.1 | Alternate limit is 155 ppmvd at 3% O2 | Applies to box or cabin type units, and vertical cylindrical process heaters
| Boilers, Steam Generators, and Process Heaters | NOx | > 5 | MMBtu/hr | Gaseous fuel | 0.036 | lb/MMBtu | Rule 4305, 5.1.1 | Alternate limit is 30 ppmvd at 3% O2 | Applies units except box or cabin type units, and vertical cylindrical process heaters
| Boilers, Steam Generators, and Process Heaters | NOx | > 5 | MMBtu/hr | Liquid fuel | 0.052 | lb/MMBtu | Rule 4305, 5.1.1 | Alternate limit is 40 ppmvd at 3% O2 | Applies units except box or cabin type units, and vertical cylindrical process heaters
| Boilers, Steam Generators, and Process Heaters | NOx | ≤ 20 | MMBtu/hr | Gaseous fuel | 0.018 | lb/MMBtu | Rule 4306, 5.1.A. | Alternate limit is 15 ppmvd at 3% O2 | Standard Option | Applies to all units except those in Categories C, D, E, F, G, H, and I.
| Boilers, Steam Generators, and Process Heaters | NOx | ≤ 20 | MMBtu/hr | Gaseous fuel | 0.011 | lb/MMBtu | Rule 4306, 5.1.A. | Alternate limit is 9 ppmvd at 3% O2 | Enhanced Option | Applies to all units except those in Categories C, D, E, F, G, H, and I.
| Boilers, Steam Generators, and Process Heaters | NOx | ≤ 20 | MMBtu/hr | Liquid Fuel | 0.052 | lb/MMBtu | Rule 4306, 5.1.A. | Alternate limit is 40 ppmvd at 3% O2 | Applies to all units except those in Categories C, D, E, F, G, H, and I.
| Boilers, Steam Generators, and Process Heaters | NOx | > 20 | MMBtu/hr | Gaseous fuel | 0.011 | lb/MMBtu | Rule 4306, 5.1.B. | Alternate limit is 9 ppmvd at 3% O2 | Standard Option | Applies to all units except those in Categories C, D, E, F, G, H, and I.
| Boilers, Steam Generators, and Process Heaters | NOx | > 20 | MMBtu/hr | Gaseous fuel | 0.007 | lb/MMBtu | Rule 4306, 5.1.B. | Alternate limit is 6 ppmvd at 3% O2 | Enhanced Option | Applies to all units except those in Categories C, D, E, F, G, H, and I.
| Boilers, Steam Generators, and Process Heaters | NOx | > 20 | MMBtu/hr | Liquid fuel | 0.052 | lb/MMBtu | Rule 4306, 5.1.B. | Alternate limit is 40 ppmvd at 3% O2 | Applies to all units except those in Categories C, D, E, F, G, H, and I.
| Oilfield Steam Generators | NOx | All |  | Gaseous fuel | 0.018 | lb/MMBtu | Rule 4306, 5.1.C. | Alternate limit is 15 ppmvd at 3% O2 | Standard Option
| Oilfield Steam Generators | NOx | All |  | Liquid fuel | 0.052 | lb/MMBtu | Rule 4306, 5.1.C. | Alternate limit is 40 ppmvd at 3% O2
| Refinery Units | NOx | 5 - 65 | MMBtu/hr | Gaseous fuel | 0.036 | lb/MMBtu | Rule 4306, 5.1.D. | Alternate limit is 30 ppmvd at 3% O2 | Standard Option
| Refinery Units | NOx | 5 - 65 | MMBtu/hr | Liquid fuel | 0.052 | lb/MMBtu | Rule 4306, 5.1.D. | Alternate limit is 40 ppmvd at 3% O2
| Refinery Units | NOx | 65 - 110 | MMBtu/hr | Gaseous fuel | 0.031 | lb/MMBtu | Rule 4306, 5.1.E. | Alternate limit is 25 ppmvd at 3% O2 | Standard Option
| Refinery Units | NOx | 65 - 110 | MMBtu/hr | Liquid fuel | 0.052 | lb/MMBtu | Rule 4306, 5.1.E. | Alternate limit is 40 ppmvd at 3% O2
| Refinery Units | NOx | > 110 | MMBtu/hr | Gaseous fuel | 0.018 | lb/MMBtu | Rule 4306, 5.1.F. | Alternate limit is 15 ppmvd at 3% O2 | Standard Option
| Refinery Units | NOx | > 110 | MMBtu/hr | Gaseous fuel | 0.011 | lb/MMBtu | Rule 4306, 5.1.F. | Alternate limit is 9 ppmvd at 3% O2 | Enhanced Option
| Refinery Units | NOx | > 110 | MMBtu/hr | Liquid fuel | 0.052 | lb/MMBtu | Rule 4306, 5.1.F. | Alternate limit is 40 ppmvd at 3% O2
| Load-following Units | NOx | All |  | Gaseous fuel | 0.018 | lb/MMBtu | Rule 4306, 5.1.G. | Alternate limit is 15 ppmvd at 3% O2 | Standard Option
| Load-following Units | NOx | All |  | Gaseous fuel | 0.011 | lb/MMBtu | Rule 4306, 5.1.G. | Alternate limit is 9 ppmvd at 3% O2 | Enhanced Option
| Load-following Units | NOx | All |  | Liquid fuel | 0.052 | lb/MMBtu | Rule 4306, 5.1.G. | Alternate limit is 40 ppmvd at 3% O2
| Boilers, Steam Generators, and Process Heaters | NOx | 9,000 - 30,000 | MMBtu/yr | Gaseous fuel | 0.036 | lb/MMBtu | Rule 4306, 5.1.H. | Alternate limit is 30 ppmvd at 3% O2 | Standard Option
| Boilers, Steam Generators, and Process Heaters | NOx | 9,000 - 30,000 | MMBtu/yr | Liquid fuel | 0.052 | lb/MMBtu | Rule 4306, 5.1.H. | Alternate limit is 40 ppmvd at 3% O2
| Small boilers, steam generators and process heaters | NOx | 2 - 5 | MMBtu/yr | Gaseous fuel | 0.036 | lb/MMBtu | Rule 4307, 5.1 | Alternate limit is 30 ppmvd at 3% O2
| Small boilers, steam generators and process heaters | NOx | 2 - 5 | MMBtu/yr | Liquid fuel | 0.052 | lb/MMBtu | Rule 4307, 5.1 | Alternate limit is 40 ppmvd at 3% O2
| Small boilers, steam generators and process heaters | NOx | 0.075 - 0.4 | MMBtu/yr | All | 0.093 | lb/MMBtu | Rule 4308, 5.1 | Corrected to 3% O2
| Small boilers, steam generators and process heaters | NOx | 0.4 - 2 | MMBtu/yr | All | 0.036 | lb/MMBtu | Rule 4307, 5.1 | Corrected to 3% O2

## CT
Unit | NOx Emission Limits by Size |  |  |  | Units | Regulatory Citation | Date
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Units at Major Sources 1 | 60% | 60% | 60% | 60% | % of 1990 | 22a-174-22(d)(1) | 1995-05-31
Turbine - Gas Fired | NL | NL | 55 | NL | ppmvd | 22a-174-22(e)(1) | 1995-05-31
Turbine - Other-Oil fired | NL | NL | 75 | NL | ppmvd | 22a-174-22(e)(1) | 1995-05-31
Turbine - Gas or Other-Oil Fired | NL | NL | 0.9 | 0.9 | lb/MMBtu | 22a-174-22(e)(1) | 1995-05-31
Cyclone Furnace - Gas, Oil, or Coal Fired | 0.43 | 0.43 | 0.43 | 0.43 | lb/MMBtu | 22a-174-22(e)(1) | 1995-05-31
Fast-Response Double-Furnace Naval Boiler - Gas Fired | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 22a-174-22(e)(1) | 1995-05-31
Fast-Response Double-Furnace Naval Boiler - Oil or Coal Fired | 0.3 | 0.3 | 0.3 | 0.3 | lb/MMBtu | 22a-174-22(e)(1) | 1995-05-31
Fluidized Bed Combustor - Coal Fired | 0.29 | 0.29 | 0.29 | 0.29 | lb/MMBtu | 22a-174-22(e)(1) | 1995-05-31
Other Boiler - Gas or Other-Oil Fired | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 22a-174-22(e)(1) | 1995-05-31
Other Boiler - Residual-Oil Fired | 0.25 | 0.25 | 0.25 | 0.25 | lb/MMBtu | 22a-174-22(e)(1) | 1995-05-31
Other Boiler - Coal Fired | 0.38 | 0.38 | 0.38 | 0.38 | lb/MMBtu | 22a-174-22(e)(1) | 1995-05-31
Other Fuels (i.e., other than NG, RO, DO, coal) | 0.3 | 0.3 | 0.3 | 0.3 | lb/MMBtu | 22a-174-22(e)(2)(A) | 1995-05-31
NOx Budget Sources - Non O-Season Emissions: 10/1 to 4/30 | 0.15 | NA | NA | NA | lb/MMBtu | 22a-174-22(e)(3) | 1995-05-31
1 Sources provided option of meeting 40% reduction in NOx emissions by use of allowances or emisison reduction credits [22a-174-22(a)]
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Date
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Equipment - Fuel with sulfur content < 1.0%, other than solid fuel | 1 | 1 | 1 | 1 | Wt. % Sulfur | 22a-174-19a(2)(i) | 2004-04-01
Equivalent: distillate oil (140,000 BTU/gal, 7.05 lb/gal) | 1.0061 | 1.0061 | 1.0061 | 1.0061 | lbSO2/MMBtu
Equivalent: residual oil (150,000 BTU/gal; 7.88 lb/gal) | 1.049 | 1.049 | 1.049 | 1.049 | lbSO2/MMBtu
Fuel Burning Equipment - Fuel with sulfur content < 1.0%, solid fuel | 1.1 | 1.1 | 1.1 | 1.1 | lbSO2/MMBtu
Premise with Fuel Burning Equipment - Fuel with sulfur content > 1.0%, with consent of the Commissioner | 0.55 | 0.55 | 0.55 | 0.55 | lbSO2/MMBtu | 22a-174-19a(3)(i)(A) | 2004-04-01
Fuel Burning Equipment - Fuel with sulfur content > 1.0%, with consent of the Commissioner | 1.1 | 1.1 | 1.1 | 1.1 | lbSO2/MMBtu | 22a-174-19a(3)(ii) | 2004-04-01

## DE
Unit | NOx Emission Limits by Size 1 |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Boiler - Gas only-Face & Tangential | 0.2 | 0.2 | NL | NL | lb/MMBtu | Reg. 12, Section 3.2a | May 31, 1995 - existing units
Boiler - Oil or Gas or Both-Face & Tangential | 0.25 | 0.25 | NL | NL | lb/MMBtu | Reg. 12, Section 3.2a | May 31, 1995 - existing units
Boiler - Coal/Face & Tangential -dry botom | 0.38 | 0.38 | NL | NL | lb/MMBtu | Reg. 12, Section 3.2a | May 31, 1995 - existing units
Boiler - Oil or Gas or Both-Cyclone | 0.43 | 0.43 | NL | NL | lb/MMBtu | Reg. 12, Section 3.2a | May 31, 1995 - existing units
Boiler - Coal/Stoker-dry bottom | 0.4 | 0.4 | NL | NL | lb/MMBtu | Reg. 12, Section 3.2a | May 31, 1995 - existing units
All Burners >50 and <100 MMBtu/hour: LNB or EGR
Equivalent Distillate Oil (assume 30% control from AP-42) | NL | NL | 0.1 | NL | lb/MMBtu
Equivalent Natural Gas (assume 30% control from AP-42) | NL | NL | 0.07 | NL | lb/MMBtu
All Burners >15 and <50 MMBtu/hour: Annual Tuneup
Equivalent Distillate Oil (assume 10% control from AP-42) | NL | NL | NL | 0.12857 | lb/MMBtu
Equivalent Natural Gas (Assume 10% control from AP-42) | NL | NL | NL | 0.09 | lb/MMBtu
All Combustion Units Not Exempt 2 |  |  | NL | NL |  | Reg. 42, Section 1 | 2004-05-01
May 1- September 30 | 0.1 | 0.1 | NL | NL | lb/MMBtu | Reg. 42, Section 1.c.1.A
Gas-Firing | 0.1 | 0.1 | NL | NL | lb/MMBtu | Reg. 42, Section 1.c.1.B
All Other not cover in A and B above | 0.24 | 0.24 | NL | NL | lb/MMBtu | Reg. 42, Section 1.c.1.C
Gas Turbine - Gas fuel | 42 | 42 | 42 | 42 | ppm @ 15% O2, 1-hr avg. | Reg. 12, Section 3.5 | 1995-05-31
Gas Turbine - Liquid fuel | 88 | 88 | 88 | 88 | ppm @ 15% O2, 1-hr avg. | Reg. 12, Section 3.5 | 1995-05-31
1 RACT can be set at actual emission levels higher than limits for > 100 MMBtu/hour units if LNB or EGR installed.
2 Units as of 12/12/2001 not either: in compliance with Rule 12 (Table I) Limits; equipped with LNB, FGR, SCR, or SNCR; subject to Rule 39 NOx Budget.
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Equipment, - All Fuels, New Castle County | 1 | 1 | 1 | 1 | wt % sulfur | Reg. 8, Section 2.1 | 1983-12-08
Equivalent Coal (assume 14,000 Btu/lb) | 1.4263 | 1.4263 | 1.4263 | 1.4263 | lb SO2/MMBtu
Equivalent Distillate Oil (assume 7.05 lb/gal and 140,000 Btu/gal)) | 1.0056 | 1.0056 | 1.0056 | 1.0056 | lb SO2/MMBtu
Fuel Burning Equipment - Distillate Oil, Statewide | 0.3 | 0.3 | 0.3 | 0.3 | wt % sulfur | Reg. 8, Section 2.2 | 1983-12-08
Equivalent Distillate Oil (assume 7.05 lb/gal and 140,000 Btu/gal)) | 0.30167 | 0.30167 | 0.30167 | 0.30167 | lb SO2/MMBtu

## DC
Unit | NOx Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fossil Fuel Fired Steam Generators, 2-hour limit | [5 empty] | Title 20, Section 804, App. 8-1 | > 100 MMBtu/hour
Gas | 0.2 | 0.2 | NL | NL | lb/MMBtu
Liquid | 0.3 | 0.3 | NL | NL | lb/MMBtu
Solid | 0.7 | 0.7 | NL | NL | lb/MMBtu
Fossil Fuel Fired Steam Generators -annual tuning | [5 empty] | Title 20, Section 805.5(a) | < 20 MMBtu/hour
Equivalent Distillate Oil (assume 10% control from AP-42) | NL | NL | NL | 0.12857 | lb/MMBtu
Equivalent Natural Gas (Assume 10% control from AP-42) | NL | NL | NL | 0.09 | lb/MMBtu
Fossil Fuel Fired Steam Generators, 24 hour limits
Oil, tangential or face -fired | NL | NL | 0.3 | NL | lb/MMBtu | Title 20, Section 805.5(b) | > 50 MMBtu/hr & < 100 MMBtu/hr
Dry Bottom Coal: tangential, face-fired, or stoker -fired | 0.43 | 0.43 | NL | NL | lb/MMBtu | Title 20, Section 805.5(c)(1) | > 100 MMBtu/hour
Natural Gas: tangential or face-fired | 0.2 | 0.2 | NL | NL | lb/MMBtu | Title 20, Section 805.5(c)(2) | > 100 MMBtu/hour
Oil or Oil & Gas: tangential or face- fired | 0.25 | 0.25 | NL | NL | lb/MMBtu | Title 20, Section 805.5(c) | > 100 MMBtu/hour
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Oil and Coal | 1 | 1 | 1 | 1 | wt % sulfur | Title 20, Section 801.1 & 802.1 | -
Equivalent Coal (assume 14,000 BTU/lb) | 1.4263 | 1.4263 | 1.4263 | 1.4263 | lb SO2/MMBtu
Equivalent Oil (assume 7.05 lb/gal, 140,000 btu/gal) | 1.0056 | 1.0056 | 1.0056 | 1.0056 | lb SO2/MMBtu
Sulfur process emissions | 0.05 | 0.05 | 0.05 | 0.05 | vol % | Title 20, Section 803.1 | -

## ME
Unit | NOx Emission Limits by Size 1 |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Boiler >1,500 MMBtu/hr All Fuels Statewide | 0.3 | NL | NL | NL | lb/MMBtu | 6-96-138.3(A) | Effective 31-May-95
Boiler > 20 & < 50 MMBtu/hr All Fuels Statewide - annual tune up | [5 empty] | 6-96-138.3(I)
Equivalent Distillate Oil (assume 10% control & AP-42 Emissions) | NL | NL | NL | 0.12857 | lb/MMBtu
Equivalent Natural Gas (Assume 10% control & AP-42 Emissions) | NL | NL | NL | 0.09 | lb/MMBtu
Equivalent Biomass (assume 10% control & AP-42 Emissions for dry wood) | NL | NL | NL | 0.441 | lb/MMBtu
Boilers > 50 & < 1,500 MMBtu/hour in Moderate Non-Attainment Areas
biomass; biomass and other than coal and oil. | 0.3 | 0.3 | 0.3 | NL | lb/MMBtu | 6-96-138.3(B)
oil; biomass & oil | 0.4 | 0.4 | 0.4 | NL | lb/MMBtu | 6-96-138.3(B)
biomass & coal | 0.45 | 0.45 | 0.45 | NL | lb/MMBtu | 6-96-138.3(B)
Boilers > 50 & < 1,500 MMBtu/hour in Attainment Areas
oil; biomass; biomas & oil; biomass & other than coal & oil | 0.3 | 0.3 | 0.3 | NL | lb/MMBtu | 6-96-138.4
biomass & coal | 0.45 | 0.45 | 0.45 | NL | lb/MMBtu | 6-96-138.4
EGU - Fossil Fuel (≥ 25 MW, heat input <750 MMBtu/hr) | 0.22 | NL | NL | NL | lb/MMBtu | 6-96-145.3(B)(2)(a) | Effective January 1, 2005 in Counties not waived under section 182(f) of the 1990 CAAA (Applies in York, Cumberland, Sagadahoc, Androscoggin, Kennebec, Lincoln and Knox)
EGU - Fossil Fuel (≥ 25 MW, heat inputs ≥ 750 MMBtu/hr)) | 0.15 | NL | NL | NL | lb/MMBtu | 6-96-145.3(B)(2)(b)
Non-EGU Fossil Fuel-Fired Indirect heat Exchangers > 250 MMBtu/hour | 0.2 | NL | NL | NL | lb/MMBtu | 6-96-145.3(B)(2)(c)
1 Sources can petition for less stringent, alternative limit [6-96-145.3(D)]
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Liquid Fossil Fuels | 2 | 2 | 2 | 2 | wt % sulfur | 6-96-106.2(A)(2) | Effective 1-Nov-91, statewide
Equivalent Distillate Oil (7.05 lb/gal, 140,000 Btu/gal) | 2.0111 | 2.0111 | 2.0111 | 2.0111 | lb SO2/MMBtu
Liquid Fossil Fuels | 1.5 | 1.5 | 1.5 | 1.5 | wt % sulfur | 6-96-106.2(A)(3) | Applies to the Portland Peninsula AQR only
Equivalent Distillate Oil (7.05 lb/gal, 140,000 Btu/gal) | 1.5084 | 1.5084 | 1.5084 | 1.5084 | lb SO2/MMBtu
Solid Fossil Fuels | 0.96 | 0.96 | 0.96 | 0.96 | lb S/MMBtu | 6-96-106.2(B)(2) | Effective 1-Nov-91, statewide
Equivalent Coal (14,000 Btu/lb) | 1.917 | 1.917 | 1.917 | 1.917 | lb SO2/MMBtu
Solid Fossil Fuels | 0.72 | 0.72 | 0.72 | 0.72 | lb S/MMBtu | 6-96-106.2(B)(3) | Applies to the Portland Peninsula AQR only
Equivalent Coal (14,000 Btu/lb) | 1.4378 | 1.4378 | 1.4378 | 1.4378 | lb SO2/MMBtu
Fuel Burning Equipment - All Fuels | 1.92 | 1.92 | 1.92 | 1.92 | lb SO2/MMBtu | 6-96-106.4(B) | Effective 1-Nov-91, statewide; When using FGD or other sulfur removal device, i.e., exempt from 6-96-106.2 fuel sulfur content
Fuel Burning Equipment - All Fuels | 1.57 | 1.57 | 1.57 | 1.57 | lb SO2/MMBtu | 6-96-106.4(C) | Applies to the Portland Peninsula AQR only; When using FGD or other sulfur removal device, i.e., exempt from 6-96-106.2 fuel sulfur content

## MD
Unit | NOx Emission Limits by Size 1 |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Equipment - Natural Gas | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 26.11.09.08(B)(1)(c) | Units located at premises that have total potential to emit: (a) 25 tons or more per year of NOx and is located in Baltimore City, or Anne Arundel, Baltimore, Calvert, Carroll, Cecil, Charles, Frederick, Harford, Howard, Montgomery, or Prince George's counties; or (b) 100 tons or more per year of NOx and is located in Allegany, Caroline, Dorchester, Garrett, Kent, Queen Anne's, St. Mary's, Somerset, Talbot, Washington, Wicomico, or Worcester counties.
Fuel Burning Equipment - Oil/Natural Gas | 0.25 | 0.25 | 0.25 | 0.25 | lb/MMBtu | 26.11.09.08(B)(1)(c)
Fuel Burning Equipment - Coal, dry bottom | 0.38 | 0.38 | 0.38 | 0.38 | lb/MMBtu | 26.11.09.08(B)(1)(c)
Fuel Burning Equipment - Coal, wet bottom | 1 | 1 | 1 | 1 | lb/MMBtu | 26.11.09.08(B)(1)(c)
EGU - Oil or Oil/Natural Gas | 0.3 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
EGU - Coal, tangential | 0.45 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
EGU - Coal, wall | 0.5 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
EGU - Coal, tangential (high heat release) | 0.7 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
EGU - Coal, wall (high heat release) | 0.8 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
EGU - Coal, cell burners | 0.6 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
EGU - Coal, cyclone (during ozone season) | 0.7 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
EGU - Coal, cyclone (non-ozone season) | 1.5 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
Non-EGU - All Fuels (during ozone season) | 0.7 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
Non-EGU - All Fuels (non-onzone season) | 0.99 | NL | NL | NL | lb/MMBtu | 26.11.09.08(C)(2)
Fuel Burning Equipment - Coal <250 & >100 MMBtu/hr | NL | 0.65 | NL | NL | lb/MMBtu | 26.11.09.08(D)(1)(a)
Fuel Burning Equipment - Gas <250 & >100 MMBtu/hr | NL | 0.2 | NL | NL | lb/MMBtu | 26.11.09.08(D)(1)(b)
Fuel Burning Equipment - Oil/Gas <250 & >100 MMBtu/hr | NL | 0.25 | NL | NL | lb/MMBtu | 26.11.09.08(D)(1)(b)
Fuel Burning Equipment - Annual Tuning < 100 MMBtu/hr | [5 empty] | 26.11.09.08(E)(2)
Equivalent Distillate Oil (assume 10% control from AP-42) | NL | NL | 0.12857 | 0.12857 | lb/MMBtu
Equivalent Natural Gas (assume 10% control from AP-42) | NL | NL | 0.09 | 0.09 | lb/MMBtu
Turbine - Natural Gas | 42 | 42 | 42 | 42 | ppmvd at 15% O2 | 26.11.09.08(G)(2)
Turbine - Oil | 65 | 65 | 65 | 65 | ppmvd at 15% O2 | 26.11.09.08(G)(2)
1 Provides for approval of less stringent alternative limits [26.11.09.08(B)(3)]
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Process Gas - Areas I, II, V, & VI | 0.3 | 0.3 | 0.3 | 0.3 | wt % sulfur | 26.11.09.07(A)(1)
Distillate Oil - All Areas | 0.3 | 0.3 | 0.3 | 0.3 | wt % sulfur | 26.11.09.07(A)(1) & (2)
Equivalent Distillate Oil (7.05 lb/gal, 140,000 Btu/gal) | 0.30167 | 0.30167 | 0.30167 | 0.30167 | lb SO2/MMBtu
Residual Oil - Areas I, II, V, & VI | 2 | 2 | 2 | 2 | wt % sulfur | 26.11.09.07(A)(1)
Equivalent Residual Oil (7.88 lb/gal, 150,000 Btu/gal) | 2.0111 | 2.0111 | 2.0111 | 2.0111 | lb SO2/MMBtu
Solid Fuels - Areas I, II, V, & VI | 3.5 | 3.5 | NL | NL | lb/MMBtu | 26.11.09.07(A)(1) | Only applies if all fuel burning equipment at the facility combined ≥ 100 MMBtu/hr
Residual Oil - Areas III & IV | 1 | 1 | 1 | 1 | wt % sulfur | 26.11.09.07(A)(2)
Equivalent Residual Oil (7.88 lb/gal, 150,000 Btu/gal) | 1.0056 | 1.0056 | 1.0056 | 1.0056 | lb SO2/MMBtu
Solid Fuels - Areas III & IV | 1 | 1 | 1 | 1 | wt % sulfur | 26.11.09.07(A)(2)
Equivalent Coal (14,000 BTU/lb) | 1.4263 | 1.4263 | 1.4263 | 1.4263 | lb SO2/MMBtu
Solid Fuels - Areas III & IV | 3.5 | NL | NL | NL | lb SO2/MMBtu | 26.11.09.07(B)(4) | Applies to existing cyclone type fuel burning equipment with heat inputs > 1,000 MMBtu/hr
Area I: The western area of the State comprising the counties of Allegany, Garrett, and Washington.
Area II: The central area of the State composed of Frederick County.
Area III: The Baltimore metropolitan area of the State comprising Baltimore City and the counties of Anne Arundel, Baltimore, Carroll, Harford, and Howard.
Area IV: The Washington metropolitan area of the State comprising the counties of Montgomery and Prince George's.
Area V: The southern area of the State comprising the counties of Calvert, Charles, and St. Mary's.
Area VI: The eastern shore area of the State comprising the counties of Caroline, Cecil, Dorchester, Kent, Queen Anne's, Somerset, Talbot, Wicomico, and Worcester.

## MA
Unit | NOx Emission Limits by Size 1 |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Boiler - Natural Gas | 0.2 | 0.2 | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Oil or Oil/Natural Gas (Heat Release ≤ 70,000 BTU/hrs-ft3) | NL | 0.3 | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Oil or Oil/Natural Gas (Heat Release > 70,000 BTU/hrs-ft3) | NL | 0.4 | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Natural Gas, tangential | 0.2 | NL | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Oil or Oil/Natural Gas, tangential | 0.25 | NL | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Oil/Natural Gas, face | 0.28 | NL | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Solid fuel other than coal, stoker | 0.33 | 0.33 | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Coal, dry bottom - tangential | 0.38 | 0.38 | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Coal, dry bottom - face | 0.45 | 0.45 | NL | NL | lb/MMBtu | 310 CMR 7.19(4)(a) | Effective 31-May-95
Boiler - Oil/Natural Gas, repowered | 0.1 | 0.1 | 0.1 | 0.1 | lb/MMBtu | 310 CMR 7.19(4)(b) | Effective 31-May-95
Boiler - Solid fuel, dry bottom - face/tangential, repowered | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 310 CMR 7.19(4)(b) | Effective 31-May-95
Boiler - Natural Gas, face/tangential | NL | NL | 0.1 | NL | lb/MMBtu | 310 CMR 7.19(5)(a) | Effective 31-May-95
Boiler - Distillate Oil or Distillate Oil/Natural Gas, face/tangential | NL | NL | 0.12 | NL | lb/MMBtu | 310 CMR 7.19(5)(a) | Effective 31-May-95
Boiler - Residual Oil or Residual Oil/Natural Gas, face/tangential 2 | NL | NL | 0.3 | NL | lb/MMBtu | 310 CMR 7.19(5)(a) | Effective 31-May-95
Boiler - Solid Fuel, face/tangential/stoker | NL | NL | 0.43 | NL | lb/MMBtu | 310 CMR 7.19(5)(a) | Effective 31-May-95
Fuel Burning Equipment - Annual Tuning < 50 & > 20 MMBtu/hr | [5 empty] | 310 CMR 7.19(6)(a) | Effective 31-May-95
Estimate Equivalent Distillate Oil (assume 10% control from AP-42) | NL | NL | NL | 0.12857 | lb/MMBtu
Estimate Equivalent Natural Gas (assume 10% control from AP-42) | NL | NL | NL | 0.09 | lb/MMBtu
Boiler - new units after 9/14/2001 at Non-Title V Permitted Facilities < 40 & > 10 MMBtu/hr | [5 empty] | 310 CMR 7.26(30)
Natural Gas | NL | NL | NL | 0.035 | lb/MMBtu
Distillate Oil (max on oil: 90 Days/yr) | NL | NL | NL | 0.15 | lb/MMBtu
Turbine - Natural Gas, combined cycle | 42 | 42 | 42 | 42 | ppmvd at 15% O2 | 310 CMR 7.19(7)(a) | Effective 31-May-95
Turbine - Oil, combined cycle | 65 | 65 | 65 | 65 | ppmvd at 15% O2 | 310 CMR 7.19(7)(a) | Effective 31-May-95
Turbine - Oil/Natural Gas, combined cycle | 50 | 50 | 50 | 50 | ppmvd at 15% O2 | 310 CMR 7.19(7)(a) | Effective 31-May-95
Turbine - Natural Gas, simple cycle | 65 | 65 | 65 | 65 | ppmvd at 15% O2 | 310 CMR 7.19(7)(a) | Effective 31-May-95
Turbine - Oil or Oil/Natural Gas, simple cycle | 100 | 100 | 100 | 100 | ppmvd at 15% O2 | 310 CMR 7.19(7)(a) | Effective 31-May-95
1 Provides for approval of less stringent alternative limits [310 CMR 7.19(4)(c)]
2 Allows exhaust gas recirculation and oxygen control as compliance alternative to limit [310 CMR 7.19(5)(a)(2)(c)(ii)]
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fossil Fuel - Berkshire APCD and remainder of Merrimack Valley APCD (1.21 lbs S /MMBtu) | 2.42 | 2.42 | 2.42 | 2.42 | lb SO2 /MMBtu | 310 CMR 7.05(1)(a) | -
Fossil Fuel - City of Worcester, remainder of Central MAPCD, City of Lawrence, Towns of Andover, North Andover, and Methuen, remainder of Metropolitan Boston APCD, Pioneer Valley APCD, and Southeastern MAPCD (0.55 lb S /MMBtu) | 1.1 | 1.1 | 1.1 | 1.1 | lb SO2 /MMBtu | 310 CMR 7.05(1)(a) | -
Fossil Fuel - Cities and Towns of Arlington, Belmont, Boston, Brookline, Cambridge, Chelsea, Everett, Malden, Medford, Newton, Somerville, Waltham, and Watertown (0.28 lb S /MMBtu) | 0.56 | 0.56 | 0.56 | 0.56 | lb SO2 /MMBtu | 310 CMR 7.05(1)(a) | -
Distillate Fuel Oil (0.17 lb S /MMBtu) | 0.34 | 0.34 | 0.34 | 0.34 | lb SO2 /MMBtu | 310 CMR 7.05(1)(a) | -
Fossil Fuel (1.21 lb S /MMBtu) | 2.42 | 2.42 | NL | NL | lb SO2 /MMBtu | 310 CMR 7.05(1)(b) | -
EGU located in the cities and towns of Arlington, Belmont, Boston, Brookline, Cambridge, Chelsea, Everett, Malden, Medford, Newton, Somerville, Waltham, and Watertown - Fossil Fuel (0.55 lb S /MMBtu) | 1.1 | NL | NL | NL | lb SO2 /MMBtu (for units > 2,500 MMBtu/hr) | 310 CMR 7.05(1)(b) | -
Fuel Burning Equipment - Fossil Fuel (1.21 lbs S/MMBtu) | 2.4 | 2.4 | NL | NL | lb SO2 /MMBtu | 310 CMR 7.22(1) | Effective 31-Dec-94
Boiler - new units after 9/14/2001 at Non-Title V Permitted Facilities < 40 & > 10 MMBtu/hr | [5 empty] | 310 CMR 7.26(30)
Natural Gas | NL | NL | NL | 0.0006 | lb SO2 /MMBtu
Distillate Oil (max on oil: 90 Days./yr, 0.05 wt. % sulfur) | NL | NL | NL | 0.050571 | lb SO2 /MMBtu

## NH
Unit | NOx Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Utility Boiler - Coal, wet bottom - tangential/face | 1 | 1 | 1 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Coal, wet bottom - cyclone (< 320 MW) | 0.92 | 0.92 | 0.92 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Coal, wet bottom - cyclone (> 320 MW) 1 | 1.4 | 1.4 | 1.4 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Coal, dry bottom - tangential | 0.38 | 0.38 | 0.38 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Coal, dry bottom - face | 0.5 | 0.5 | 0.5 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Coal, dry bottom - stoker | 0.3 | 0.3 | 0.3 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Oil, tangential/face | 0.35 | 0.35 | 0.35 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Oil/Natural Gas, tangential/face | 0.25 | 0.25 | 0.25 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Natural Gas | 0.2 | 0.2 | 0.2 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Wood or Wood/Oil, moving grate | 0.33 | 0.33 | 0.33 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Boiler - Wood or Wood/Oil, stationary grate | 0.25 | 0.25 | 0.25 | NL | lb/MMBtu | Env-A 1211.03(c) | Effective 31-Dec-89
Utility Steam Electric, Auxiliary, & Industrial Boilers - > 50 & < 5 MMBtu/hr Annual Tuning | NL | NL | NL |  |  | Env-A 1211.03(b), 04(b), 05(c), & 12(b) | Effective 31-May-95
Equivalent Distillate Oil (assume 10% control from AP-42) | NL | NL | NL | 0.12857 | lb/MMBtu
Equivalent Natural Gas (assume 10% control from AP-42) | NL | NL | NL | 0.09 | lb/MMBtu
Industrial/Steam Electric Boiler - Coal or Coal/Other, wet bottom - tangential/face | 1 | 1 | NL | NL | lb/MMBtu | Env-A 1211.04(d) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Coal or Coal/Other, wet bottom - cyclone | 0.92 | 0.92 | NL | NL | lb/MMBtu | Env-A 1211.04(d) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Coal or Coal/Oil, dry bottom - tangential | 0.38 | 0.38 | 0.38 | NL | lb/MMBtu | Env-A 1211.04(c), 4(d), 5(c) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Coal or Coal/Oil, dry bottom - face | 0.5 | 0.5 | 0.5 | NL | lb/MMBtu | Env-A 1211.04(c), 4(d), 5(c) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Coal or Coal/Oil, dry bottom - stoker | 0.3 | 0.3 | 0.3 | NL | lb/MMBtu | Env-A 1211.04(c), 4(d), 5(c) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Distillate Oil or Oil/Natural Gas on No. 2 Oil or Combination of Gas/Oil, tangential/face 2 | NL | NL | 0.12 | NL | lb/MMBtu | Env-A 1211.04(c) & 5(c) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Residual Oil or Oil/Natural Gas on Residual Oil or Combination Gas/Oil, tangential/face 2 | NL | NL | 0.3 | NL | lb/MMBtu | Env-A 1211.04(c) & 5(c) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Natural Gas or Oil/Natural Gas on Natural Gas, tangential/face 2 | NL | NL | 0.1 | NL | lb/MMBtu | Env-A 1211.04(c) & 5(c) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Oil, tangential/face 2 | 0.3 | 0.3 | NL | NL | lb/MMBtu | Env-A 1211.04(d) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Gas or any Combination Gas/Oil, tangential/face 2 | 0.25 | 0.25 | NL | NL | lb/MMBtu | Env-A 1211.04(d) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler- Natural Gas 2 | 0.1 | 0.1 | NL | NL | lb/MMBtu | Env-A 1211.04(d) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Wood or Wood/Oil, moving grate | 0.33 | 0.33 | 0.33 | NL | lb/MMBtu | Env-A 1211.04(c), 4(d), 5(c) & 5(d) | Effective 31-Dec-89
Industrial/Steam Electric Boiler - Wood or Wood/Oil, stationary grate | 0.25 | 0.25 | 0.25 | NL | lb/MMBtu | Env-A 1211.04(c), 4(d), 5(c) & 5(d) | Effective 31-Dec-89
Auxillary Boiler - All Fuels | 0.2 | 0.2 | 0.2 | NL | lb/MMBtu | Env-A 1211.12(c) | Effective 31-Dec-89
Turbine - Natural Gas, combined or regenerative cycle | 42 / 0.155 | 42 / 0.155 | 42 / 0.155 | 42 / 0.155 | ppmvd at 15% O2 / lb/MMBtu | Env-A 1211.06(c) | Effective 31-Dec-89
Turbine - Oil, combined or regenerative cycle | 65 / 0.253 | 65 / 0.253 | 65 / 0.253 | 65 / 0.253 | ppmvd at 15% O2 / lb/MMBtu | Env-A 1211.06(c) | Effective 31-Dec-89
Turbine - Natural Gas, simple cycle | 55 / 0.203 | 55 / 0.203 | 55 / 0.203 | 55 / 0.203 | ppmvd at 15% O2 / lb/MMBtu | Env-A 1211.06(c) | Effective 31-Dec-89
Turbine - Oil, simple cycle | 75 / 0.292 | 75 / 0.292 | 75 / 0.292 | 75 / 0.292 | ppmvd at 15% O2 / lb/MMBtu | Env-A 1211.06(c) | Effective 31-Dec-89
Turbine - Natural Gas | 25 / 0.092 | 25 / 0.092 | 25 / 0.092 | 25 / 0.092 | ppmvd at 15% O2 / lb/MMBtu | Env-A 1211.06(c) | Post 27-May-99
1 Or alternatively, install SNCR or equivalent [Env-A 1211.03(c)(1)(b)(2)]
2 Or alternatively, install LNB or equivalent [Env-A 1211.053(c)(2), (c)(3), (c)(4), (d)(3) & (d)(4) ]
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
No. 2 Oil and JP-4 aviation fuel (Limit: 0.4 wt. % Sulfur) | 0.40286 | 0.40286 | 0.40286 | 0.40286 | lb SO2 /MMBtu | Env-A 1604.01(a) | Effective 23-Apr-05
No. 4 Oil (Limit 1.0 wt. % Sulfur) | 1.0297 | 1.0297 | 1.0297 | 1.0297 | lb SO2 /MMBtu | Env-A 1604.01(b) | Effective 23-Apr-05
No. 5, 6, and crude Oils - Coos County (Limit: 2.2 wt. % sulfur) | 2.3115 | 2.3115 | 2.3115 | 2.3115 | lb SO2 /MMBtu | Env-A 1604.01(c) | Effective 23-Apr-05
No. 5, 6, and crude Oils - Remainder of State (Limit: 2.0 wt. % sulfur) | 2.1013 | 2.1013 | 2.1013 | 2.1013 | lb SO2 /MMBtu | Env-A 1604.01(c) | Effective 23-Apr-05
Jet A, A-1, B, and JP-8 aviation fuels (Limit: 0.3 wt. % Sulfur) | 0.29538 | 0.29538 | 0.29538 | 0.29538 | lb SO2 /MMBtu | Env-A 1604.01(f) | Effective 23-Apr-05
Gaseous Fuels (Limit: 15 grains/100 scf) | 0.042857 | 0.042857 | 0.042857 | 0.042857 | lb SO2 /MMBtu | Env-A 1605.01 | Effective 23-Apr-05
Coal (Max 2.8 lbs S/MMBtu; 3-mon ave 2.0 lbs S/MMBtu) | 4 | 4 | 4 | 4 | lb SO2 /MMBtu, (3-month) | Env-A 1606.01(a) | Device in Operation before 15-Apr-70
Coal (Max 1.5 lbs S/MMBtu; 3-mon ave 1.0 lbs S/MMBtu) | 2 | 2 | 2 | 2 | lb SO2 /MMBtu (3-month) | Env-A 1606.01(b) | Device in Operation after 15-Apr-70

## NJ
Unit | NOx Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Utility Boiler - Coal, wet bottom - tangential/face 1 | 1 | 1 | 1 | 1 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Coal, wet bottom - cyclone 1 | 0.6 | 0.6 | 0.6 | 0.6 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Coal, dry bottom - tangential 1 | 0.38 | 0.38 | 0.38 | 0.38 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Coal, dry bottom - face 1 | 0.45 | 0.45 | 0.45 | 0.45 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Coal, dry bottom - cyclone 1 | 0.55 | 0.55 | 0.55 | 0.55 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Oil and/or Gas, tangential 1 | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Oil and/or Gas, face 1 | 0.28 | 0.28 | 0.28 | 0.28 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Oil and/or Gas, cyclone 1 | 0.43 | 0.43 | 0.43 | 0.43 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Gas only, tangential/face 1 | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Utility Boiler - Gas only, cyclone 1 | 0.43 | 0.43 | 0.43 | 0.43 | lb/MMBtu | 7:27-19.4(a) | 2000-06-06
Gas Turbine - Oil, stationary simple cycle 2 | 0.4 | 0.4 | 0.4 | 0.4 | lb/MMBtu | 7:27-19.5(a) | 2000-06-06
Gas Turbine - Gas, stationary simple cycle 2 | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 7:27-19.5(a) | 2000-06-06
Gas Turbine - Oil, stationary combined or regenerative cycle 2 | 0.35 | 0.35 | 0.35 | 0.35 | lb/MMBtu | 7:27-19.5(b) | 2000-06-06
Gas Turbine - Gas, stationary combined or regenerative cycle 2 | 0.15 | 0.15 | 0.15 | 0.15 | lb/MMBtu | 7:27-19.5(b) | 2000-06-06
Non-Utility Boiler - Coal, wet bottom - tangential/face 3 | 1 | 1 | 1 | 1 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Coal, wet bottom - cyclone 3 | 0.6 | 0.6 | 0.55 | 0.55 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Coal, dry bottom - tangential 3 | 0.38 | 0.38 | 0.38 | 0.38 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Coal, dry bottom - face 3 | 0.45 | 0.45 | 0.43 | 0.43 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Coal, dry bottom - cyclone 3 | 0.55 | 0.55 | 0.55 | 0.55 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - No. 2 Oil, tangential/face/cyclone 3 | NL | NL | 0.12 | 0.12 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Other Liquid Fuels, tangential/face/cyclone 3 | NL | NL | 0.3 | 0.3 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Refinery Fuel Gas, tangential/face/cyclone 3 | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Natural Gas, tangential/face 3 | 0.1 | 0.1 | 0.1 | 0.1 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Natural Gas, cyclone 3 | 0.1 | 0.1 | 0.1 | 0.1 | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Oil and/or Gas, tangential 3 | 0.2 | 0.2 | NL | NL | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Oil and/or Gas, face 3 | 0.28 | 0.28 | NL | NL | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
Non-Utility Boiler - Oil and/or Gas, cyclone 3 | 0.43 | 0.43 | NL | NL | lb/MMBtu | 7:27-19.7(h) | 2007-03-07
1 Alternative limits can be authorized including provisions for emission averaging and fuel switching [ 7:27-19.4(a) ]
2 Alternative limits can be authorized including provisions for emission averaging and fuel switching [ 7:27-19.5(a) & 5(b)]
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Equipment - No. 2 Oil, Zones 1, 2, & 5 | 0.32 | 0.32 | 0.32 | 0.32 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Fuel Burning Equipment - No. 2 Oil, Zones 3, 4, & 6 | 0.21 | 0.21 | 0.21 | 0.21 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Fuel Burning Equipment - No. 4 Oil, Zone 1 | 2.1 | 2.1 | 2.1 | 2.1 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Fuel Burning Equipment - No. 4 Oil, Zones 2 & 5 | 0.74 | 0.74 | 0.74 | 0.74 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Fuel Burning Equipment - No. 4 Oil, Zones 3, 4, & 6 | 0.32 | 0.32 | 0.32 | 0.32 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Fuel Burning Equipment - No. 5, 6, & heavier oils, Zone 1 | 2.1 | 2.1 | 2.1 | 2.1 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Fuel Burning Equipment - No. 5, 6, & heavier oils, Zones 2 & 5 | 1.05 | 1.05 | 1.05 | 1.05 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Fuel Burning Equipment - No. 5, 6, & heavier oils, Zone 3 | 0.53 | 0.53 | 0.53 | 0.53 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Fuel Burning Equipment - No. 5, 6, & heavier oils, Zones 4 & 6 | 0.32 | 0.32 | 0.32 | 0.32 | lb SO2/MMBtu | 7:27-9.2(c) | 1978-10-12
Zone 1: Atlantic, Cape May, Cumberland, and Ocean Counties.
Zone 2: Hunterdon, Sussex, and Warren Counties.
Zone 3: Burlington, Camden, Gloucester, and Mercer Counties except those municipalities included in Zone 6.
Zone 4: Bergen, Essex, Hudson, Middlesex, Monmouth, Morris, Passaic, Somerset, and Union Counties.
Zone 5: Salem County.
Zone 6: Burlington County, the municipalities of Bass River Township, Shamong Township, Southampton Township, Tabernacle Township, Washington Township, Woodland Township, and in Camden County, Waterford Township.

## NY
Unit | NOx Emission Limits by Size 1 |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Boilers - Gas only | 0.2 | 0.2 | 0.1 | NL | lb/MMBtu | 227-2.4(a)(1), (b)(1), & (c)(2) | 2004-02-11
Boilers - Gas/Oil - Tangential/Wall Fired | 0.25 | 0.3 | NL | NL | lb/MMBtu | 227-2.4(a)(1) & (b)(1) | 2004-02-11
Boilers - Gas/Oil - Cyclone | 0.43 | 0.3 | NL | NL | lb/MMBtu | 227-2.4(a)(1) & (b)(1) | 2004-02-11
Boilers - Distillate Oil | NL | NL | 0.12 | NL | lb/MMBtu | 227-2.4(c)(2) | 2004-02-11
Boilers - Residual Oil | NL | NL | 0.3 | NL | lb/MMBtu | 227-2.4(c)(2) | 2004-02-11
Boilers - Coal - Tangential/Wall Fired, wet bottom | 1 | NL | NL | NL | lb/MMBtu | 227-2.4(a)(1) | 2004-02-11
Boilers - Coal - Cyclone, wet bottom | 0.6 | NL | NL | NL | lb/MMBtu | 227-2.4(a)(1) | 2004-02-11
Boilers - Coal - Tangential Fired, dry bottom | 0.42 | NL | NL | NL | lb/MMBtu | 227-2.4(a)(1) | 2004-02-11
Boilers - Coal - Wall Fired, dry bottom | 0.45 | NL | NL | NL | lb/MMBtu | 227-2.4(a)(1) | 2004-02-11
Boilers - Coal - Stoker, dry bottom | 0.3 | NL | NL | NL | lb/MMBtu | 227-2.4(a)(1) | 2004-02-11
Boilers - Coal - Stoker, dry bottom w/ 25% or more other fuels | 0.33 | NL | NL | NL | lb/MMBtu | 227-2.4(a)(1) | 2004-02-11
Boilers - Pulverized Coal | NL | 0.5 | NL | NL | lb/MMBtu | 227-2.4(b)(1) | 2004-02-11
Boilers - Coal - Overfeed Stoker | NL | 0.3 | NL | NL | lb/MMBtu | 227-2.4(b)(1) | 2004-02-11
Boilers - Coal - Overfeed Stoker w/ 25% or more other fuels | NL | 0.33 | NL | NL | lb/MMBtu | 227-2.4(b)(1) | 2004-02-11
Boilers - Annual Tuning > 10 & < 50 MMBtu/hr | [5 empty] | 227-2.4(d) | 2004-02-11
Equivalent Distillate Oil (assume 10% control from AP-42) | NL | NL | NL | 0.12857 | lb/MMBtu
Equivalent Natural Gas (assume 10% control from AP-42) | NL | NL | NL | 0.09 | lb/MMBtu
Combustion Turbine - Gas Only, simple cycle/regenerative | 50 | 50 | 50 | 50 | ppmvd | 227-2.4(e)(1)(i) | 2004-02-11
Combustion Turbine - Multiple Fuels, simple cycle/regenerative | 100 | 100 | 100 | 100 | ppmvd | 227-2.4(e)(1)(ii) | 2004-02-11
Combustion Turbine - Gas, combined cycle | 42 | 42 | 42 | 42 | ppmvd | 227-2.4(e)(2)(i) | 2004-02-11
Combustion Turbine - Oil, combined cycle | 65 | 65 | 65 | 65 | ppmvd | 227-2.4(e)(2)(ii) | 2004-02-11
1 Alternative limits can be set thru case-by-case RACT determinations [227-2.4]
Unit | SO2 Emission Limits by Size 1 |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Equipment - Oil (Limit: 0.75 wt. % S) | 0.75536 | NL | NL | NL | lb SO2/MMBtu | 225-1.2(a)(1) | Units constructed after 3-Mar-73, not located in New York City, or Nassau, Rockland, or Westchester Counties
Fuel Burning Equipment - Coal (Limit: 0.6 lb S/MMBtu) | 1.2 | NL | NL | NL | lb SO2/MMBtu | 225-1.2(a)(1) | Units constructed after 3-Mar-73, not located in New York City, or Nassau, Rockland, or Westchester Counties
Residual Oil - New York City (Limit: 0.3 wt. % S) | 0.3152 | 0.3152 | 0.3152 | 0.3152 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Distillate Oil - New York City (Limit: 0.2 wt. % S) | 0.20143 | 0.20143 | 0.20143 | 0.20143 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Coal - New York City, Nassau, Rockland, & Westchester Counties (Limit: 0.2 lbs S/MMBtu) | 0.4 | 0.4 | 0.4 | 0.4 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Oil - Nassau, Rockland, & Westchester Counties (Limit 0.37 wt. % S) | 0.37264 | 0.37264 | 0.37264 | 0.37264 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Oil - Suffolk County: Town of Babylon, Brookhaven, Huntington, Islip, & Smith Town (Limit: 1 wt. % S) | 1.0114 | 1.0114 | 1.0114 | 1.0114 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Coal - Suffolk County: Town of Babylon, Brookhaven, Huntington, Islip, & Smith Town (Limit: 0.6 lbs S/MMBtu) | 1.2 | 1.2 | 1.2 | 1.2 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Oil - Erie County: City of Lackawana & South Buffalo (Limit: 1.1 wt. % S) | 1.1079 | 1.1079 | 1.1079 | 1.1079 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Coal - Niagara County & Erie County (Limit: 3-month average 1.4 lbs S/MMBtu) | 2.8 | 2.8 | 2.8 | 2.8 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Oil - Niagara County, Remainder of Erie County, and Remainder of State (Limit: 1.5 wt. % S) | 1.5107 | 1.5107 | 1.5107 | 1.5107 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
Coal - Remainder of State Limit: annual ave. 1.7 lbs S/MMBtu) | 3.4 | 3.4 | 3.4 | 3.4 | lb SO2/MMBtu | 225-1.2(d) | Effective after 1-Jan-88
1 Allows alternative limits based on "impact offset plans" (bubble) for two or more units at same facility with > 100 tons/yr emissions or 50 MW or capacity [225-1.3]

## PA
Unit | NOx Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Boiler - NG or non-commercial gas | NL | 0.1 | NL | NL | lb/MMBtu | 129.201(c)(1)(i) | 1-May-05, for boilers located in Bucks, Chester, Delaware, Montgomery or Philadelphia County
Boiler - Solid or Liquid Fuel | NL | 0.2 | NL | NL | lb/MMBtu | 129.201(c)(1)(ii) | 1-May-05, for boilers located in Bucks, Chester, Delaware, Montgomery or Philadelphia County
Boiler - All fuels | 0.17 | NL | NL | NL | lb/MMBtu | 129.201(c)(2) | 1-May-05, for boilers located in Bucks, Chester, Delaware, Montgomery or Philadelphia County and not subject to NOx Budget Rules
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Combustion Units - All Fuels | 4 | 4 | 4 | 4 | lb SO2/MMBtu, 1-hr period | 123.22(a)(1), 123.22(b)(1) | Nonair basin areas, Erie, Harrisburg, York, Lancaster, Scranton, and Wilkes-Barre air basins
Combustion Units - No. 2 Oil & lighter fuel oils (Limit: 0.5 wt. % S) | 0.50357 | 0.50357 | 0.50357 | 0.50357 | lb SO2/MMBtu | 123.22(a)(2) | Nonair basin areas
Combustion Units - No. 4, 5, 6, & heavier fuel oils (Limit 2.8 wt. % S) | 2.9419 | 2.9419 | 2.9419 | 2.9419 | lb SO2/MMBtu | 123.22(a)(2), 123.22(b)(2)* | Nonair basin areas, Erie, Harrisburg, York, Lancaster, Scranton, and Wilkes-Barre air basins
Combustion Units - Solid Fuels | 3.7 | NL | NL | NL | lb SO2/MMBtu, 30-day running avg. | 123.22(a)(4)(iii), 123.22(b)(4)(iii) | Nonair basin areas, Erie, Harrisburg, York, Lancaster, Scranton, and Wilkes-Barre air basins
Combustion Units - Solid Fuels | 4 | NL | NL | NL | lb SO2/MMBtu, daily avg not exceeding 2-days in any 30-day period | 123.22(a)(4)(iii), 123.22(b)(4)(iii) | Nonair basin areas, Erie, Harrisburg, York, Lancaster, Scranton, and Wilkes-Barre air basins
Combustion Units - Solid Fuels | 4.8 | NL | NL | NL | lb SO2/MMBtu, maximum daily avg. | 123.22(a)(4)(iii), 123.22(b)(4)(iii) | Nonair basin areas, Erie, Harrisburg, York, Lancaster, Scranton, and Wilkes-Barre air basins
Combustion Units - No. 2 Oil & lighter fuel oils (Limit: 0.3 wt. % S) | 0.30214 | 0.30214 | 0.30214 | 0.30214 | lb SO2/MMBtu | 123.22(b)(2)*, 123.22(c)(2)* | Erie, Harrisburg, York, Lancaster, Scranton, and Wilkes-Barre air basins + Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstown air basins
Combustion Units - All Fuels | 3 | 3 | 3 | 3 | lb SO2/MMBtu, 1-hr period | 123.22(c)(1) | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstown air basins
Combustion Units - No. 4, 5, 6, & heavier fuel oils (Limit: 2 wt. % S) | 2.1013 | 2.1013 | 2.1013 | 2.1013 | lb SO2/MMBtu | 123.22(c)(2)* | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstown air basins
Combustion Units - Solid Fuels | 2.8 | NL | NL | NL | lb SO2/MMBtu, 30-day running avg. | 123.22(c)(4)(iii) | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstown air basins
Combustion Units - Solid Fuels | 3 | NL | NL | NL | lb SO2/MMBtu, daily avg not exceeding 2-days in any 30-day period | 123.22(c)(4)(iii) | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstown air basins
Combustion Units - Solid Fuels | 3.6 | NL | NL | NL | lb SO2/MMBtu, maximum daily avg. | 123.22(c)(4)(iii) | Allentown, Bethlehem, Easton, Reading, Upper Beaver Valley, and Johnstown air basins
Combustion Units - All Fuels | 0.6 (Boilers ≥ 2000 MMBtu/hr) or Formula:A=1.7xE-0.14 E=heat input (MMBtu/hr) | Formula:A=1.7xE-0.14 E=heat input (MMBtu/hr) | Formula:A=1.7xE-0.14 E=heat input (MMBtu/hr) | 1 | lb SO2/MMBtu | 123.22(d)(1), (2), & (3) | Allegheny County, Lower Beaver Valley, and Monongahela Valley air basins
Combustion Units - All Fuels | 0.60 / 1.20 | 1.00 / 1.20 | 1.00 / 1.20 | 1.00 / 1.20 | lb SO2/MMBtu (Inner Zone / Outer Zone) | 123.22(e)(1) | Southeast Pennsylvania air basin
Combustion Units - No. 2 Oil & lighter fuel oils (Limits 0.2/0.3 wt. % S) | 0.20 / 0.30 | 0.20 / 0.30 | 0.20 / 0.30 | 0.20 / 0.30 | lb SO2/MMBtu (Inner Zone / Outer Zone) | 123.22(e)(2) | Southeast Pennsylvania air basin
Combustion Units - No. 4, 5, 6, & heavier fuel oils (Limits: 0.5/1.0 wt. % S) | 0.53 / 1.1 | 0.53 / 1.1 | 0.53 / 1.1 | 0.53 / 1.1 | lb SO2/MMBtu (Inner Zone / Outer Zone) | 123.22(e)(2) | Southeast Pennsylvania air basin
Combustion Units - Noncommercial fuel | 0.60 / 1.2 | 0.60 / 1.2 | 0.60 / 1.2 | 0.60 / 1.2 | lb SO2/MMBtu (Inner Zone / Outer Zone) | 123.22(e)(3) | Southeast Pennsylvania air basin
Combustion Units - Solid Fuels | 0.45 / 0.90 | 0.75 / 0.90 | 0.75 / 0.90 | 0.75 / 0.90 | lb SO2/MMBtu, 30-day running avg. (Inner Zone / Outer Zone) | 123.22(e)(5)(iii) | Southeast Pennsylvania air basin
Combustion Units - Solid Fuels | 0.60 / 1.2 | 1.0 / 1.2 | 1.0 / 1.2 | 1.0 / 1.2 | lb SO2/MMBtu, daily avg not exceeding 2-days in any 30-day period (Inner Zone / Outer Zone) | 123.22(e)(5)(iii) | Southeast Pennsylvania air basin
Combustion Units - Solid Fuels | 0.72 / 1.44 | 1.2 / 1.44 | 1.2 / 1.44 | 1.2 / 1.44 | lb SO2/MMBtu, maximum daily avg. (Inner Zone / Outer Zone) | 123.22(e)(5)(iii) | Southeast Pennsylvania air basin
* Effective Date: August 1, 1979

## RI
Unit | NOx Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
ICI Boilers - Natural Gas | 0.1 | 0.1 | 0.1 | NL | lb/MMBtu | 27.4.2(a)(1) | 1-Jan-1990, with potential to emit 50 tpy NOx
ICI Boilers - Distillate Oil or LPG | 0.12 | 0.12 | 0.12 | NL | lb/MMBtu | 27.4.2(a)(2) | 1-Jan-1990, with potential to emit 50 tpy NOx
ICI Boilers - Residual Oil > 50 MMBtu/hr - FGR and LNB | [5 empty] | 27.4.2(b)
Equivalent Residual Oil (assum 30% control, emissions from AP-42) | 0.25667 | 0.25667 | 0.25667 | NL | lb/MMBtu
Boiler - Annual Tuning < 50 MMBtu/hr | [5 empty] | 27.4.2(c)
Equivalent Distillate Oil (assume 10% control from AP-42) | NL | NL | NL | 0.12857 | lb/MMBtu
Equivalent Natural Gas (Assume 10% control from AP-42) | NL | NL | NL | 0.09 | lb/MMBtu
Utility Boilers - Natural Gas or LPG | 0.2 | 0.2 | 0.2 | 0.2 | lb/MMBtu | 27.4.1(a) | 1-Jan-1990, with potential to emit 50 tpy NOx
Utility Boilers - Fuel Oil | 0.25 | 0.25 | 0.25 | 0.25 | lb/MMBtu | 27.4.1(b) | 1-Jan-1990, with potential to emit 50 tpy NOx
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Equipment - All fuels | 1.1 | 1.1 | 1.1 | 1.1 | lb SO2/MMBtu | 8.3.1 | 1971-10-01
Fuel Burning Equipment - Coal (Limit: 1.21 lb S/MMBtu) | 2.42 | NL | NL | NL | lb SO2/MMBtu, 30-day period | 8.3.4.1(a) & (b) | 1971-10-01
Fuel Burning Equipment - Coal (lLimit: 2.31 lb S/MMBtu) | 4.62 | NL | NL | NL | lb SO2/MMBtu, 24-hr period | 8.3.4.1(a) & (b) | 1971-10-01

## VT
Unit | NOx Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Equipment - Gaseous fossil fuel | 0.2 | NL | NL | NL | lb/MMBtu | 5-251(1)(a) | -
Fuel Burning Equipment - Liquid fossil fuel | 0.3 | NL | NL | NL | lb/MMBtu | 5-251(1)(b) | -
Fuel Burning Equipment - Solid fossil fuel | 0.7 | NL | NL | NL | lb/MMBtu | 5-251(1)(c) | -
Unit | SO2 Emission Limits by Size |  |  |  | Units | Regulatory Citation | Applicability
| Size 1 | Size 2 | Size 3 | Size 4
Fuel Burning Equipment - Liquid fossil fuel | 0.8 | NL | NL | NL | lb SO2/MMBtu | 5-252(1)(a) | -
Fuel Burning Equipment - Solid fossil fuel | 1.2 | NL | NL | NL | lb SO2/MMBtu | 5-252(1)(b) | -